## Defines (hidden)
#VERSION | 13 | 1 | 1
Define Name | Type | Comment | RTUTil Value | Excel Value
#SOL | START OF LIST
AMI_BACKGROUND |  |  | 0 | Off
|  |  | 16012 | 1 sec
|  |  | 16000 | 2 sec
|  |  | 16001 | 4 sec
|  |  | 16011 | 5 sec
|  |  | 16002 | 8 sec
|  |  | 16010 | 10 sec
|  |  | 16003 | 16 sec
|  |  | 16004 | 30 sec
|  |  | 16005 | 60 sec
|  |  | 16007 | 2 min
|  |  | 16008 | 5 min
|  |  | 16009 | 10 min
|  |  | 16013 | 15 min
DATA_TYPE_VARIANT |  |  | 16553 | Standard
|  |  | 16586 | Analog Limit Excursion
|  |  | 16554 | DB Energie TK 150
FTR_TYPE |  |  | 16098 | Disturbance recorder - SPAbus - REF542 (plus)
|  |  | 16099 | Disturbance recorder - IEC 60870-5-103
|  |  | 16101 | Undef
|  |  | 16106 | PRO - PLC file
|  |  | 16109 | Disturbance recorder - SPAbus - REx5xx
|  |  | 16203 | IEC_62056-21 Read Load profile
|  |  | 16204 | IEC_62056-21 Read Log file data
|  |  | 16257 | Sequence of recorded analog values
|  |  | 16258 | Sequence of events
|  |  | 16455 | Disturbance recorder - IEC61850 - REx630/650/670
|  |  | 16456 | Disturbance recorder - IEC61850 - REB500
|  |  | 16457 | Disturbance recorder - IEC61850 - SPAZC
|  |  | 16458 | Disturbance recorder - IEC61850 - BEN6000
|  |  | 16459 | Disturbance recorder - IEC61850 - SIEMENS Siprotec
|  |  | 16460 | Disturbance recorder - IEC61850 - AREVA P436
|  |  | 16558 | Disturbance recorder - SPAbus - REx316
|  |  | 16688 | RCD - RTU configuration data
|  |  | 16693 | Disturbance recorder - IEC61850 - REx615
|  |  | 16694 | Disturbance recorder - IEC61850 - Generic IED
|  |  | 16520 | Disturbance recorder - 500CVD90
IEC104_TRANSMISSION_FORMAT |  |  | 16090 | Normalized
|  |  | 16091 | Scaled
InputSignalTypes |  |  | 16193 | Unipolar
|  |  | 16192 | Bipolar
MODBUS_FUNCTIONCODES |  |  | 146 | 1
|  |  | 147 | 2
|  |  | 148 | 3
|  |  | 149 | 4
|  |  | 151 | 5
|  |  | 162 | 15
|  |  | 160 | 6
|  |  | 165 | 16
SIGNAL_TYPE |  |  | 1 | AMI
|  |  | 2 | BSI8
|  |  | 3 | BSI16
|  |  | 4 | BSI32
|  |  | 5 | DMI8
|  |  | 6 | DMI16
|  |  | 7 | DPI
|  |  | 8 | EPI
|  |  | 9 | ITI
|  |  | 10 | MFI
|  |  | 11 | SPI
|  |  | 12 | STI
|  |  | 13 | ASO
|  |  | 14 | BSO1
|  |  | 15 | BSO2
|  |  | 16 | BSO8
|  |  | 17 | BSO16
|  |  | 18 | DCO
|  |  | 19 | DSO8
|  |  | 20 | DSO16
|  |  | 21 | FSO
|  |  | 22 | RCO
|  |  | 23 | SCO
|  |  | 24 | SEV
|  |  | 25 | SDI
|  |  | 26 | SSC
|  |  | 27 | FTR
|  |  | 28 | TDC
|  |  | 29 | FDR
|  |  | 30 | SOC
|  |  | 31 | _End
SYSTEM_DATA_TYPE |  |  | 1 | #001
|  |  | 2 | #002
|  |  | 3 | #003
|  |  | 4 | #004
|  |  | 5 | #005
|  |  | 6 | #006
|  |  | 7 | #007
|  |  | 8 | #008
|  |  | 9 | #009
|  |  | 10 | #010
|  |  | 11 | #011
|  |  | 12 | #012
|  |  | 13 | #013
|  |  | 14 | #014
|  |  | 15 | #015
|  |  | 16 | #016: At least one indication faulty
|  |  | 17 | #017: At least one analog value faulty
|  |  | 18 | #018: At least one digital value faulty
|  |  | 19 | #019: At least one integrated total faulty
|  |  | 20 | #020: At least one object or regulation command faulty
|  |  | 21 | #021: At least one analog output faulty
|  |  | 22 | #022: At least one digital output faulty
|  |  | 23 | #023: RTU is faulty
|  |  | 24 | #024: Device/ RTU active
|  |  | 25 | #025: RTU synchronized
|  |  | 26 | #026: External clock inoperable
|  |  | 27 | #027: Local printer offline
|  |  | 28 | #028: At least one indication oscillating
|  |  | 29 | #029: Battery voltage low
|  |  | 30 | #030: AC power supply failure
|  |  | 31 | #031: At least one memory card removed
|  |  | 32 | #032: At least one user account file is missing or corrupt
|  |  | 33 | #033
|  |  | 34 | #034
|  |  | 35 | #035
|  |  | 36 | #036
|  |  | 37 | #037
|  |  | 38 | #038
|  |  | 39 | #039
|  |  | 40 | #040
|  |  | 41 | #041
|  |  | 42 | #042: Test mode active
|  |  | 43 | #043: At least one data object simulated
|  |  | 44 | #044: At least one data communication equipment (DCE) faulty
|  |  | 45 | #045: Device connected
|  |  | 46 | #046: At least one PLC function not running
|  |  | 47 | #047: At least one PLC function cycle time exceeded
|  |  | 48 | #048: Device/ RTU inoperable
|  |  | 49 | #049: Device/ RTU is out of service
|  |  | 50 | #050
|  |  | 51 | #051
|  |  | 52 | #052
|  |  | 53 | #053
|  |  | 54 | #054
|  |  | 55 | #055
|  |  | 56 | #056
|  |  | 57 | #057
|  |  | 58 | #058
|  |  | 59 | #059: Power supply failure in RTU central sub-rack
|  |  | 60 | #060: RTU A active
|  |  | 61 | #061: RTU B active
|  |  | 62 | #062: RTU A operable
|  |  | 63 | #063: RTU B operable
|  |  | 64 | #064: 1. cmd. supervision circuit disconnected or faulty
|  |  | 65 | #065: 2. cmd. supervision circuit disconnected or faulty
|  |  | 66 | #066: 3. cmd. supervision circuit disconnected or faulty
|  |  | 67 | #067: 4. cmd. supervision circuit disconnected or faulty
|  |  | 68 | #068: 5. cmd. supervision circuit disconnected or faulty
|  |  | 69 | #069: 6. cmd. supervision circuit disconnected or faulty
|  |  | 70 | #070: 7. cmd. supervision circuit disconnected or faulty
|  |  | 71 | #071: 8. cmd. supervision circuit disconnected or faulty
|  |  | 72 | #072: 9. cmd. supervision circuit disconnected or faulty
|  |  | 73 | #073: 10. cmd. supervision circuit disconnected or faulty
|  |  | 74 | #074: 11. cmd. supervision circuit disconnected or faulty
|  |  | 75 | #075: 12. cmd. supervision circuit disconnected or faulty
|  |  | 76 | #076: 13. cmd. supervision circuit disconnected or faulty
|  |  | 77 | #077: 14. cmd. supervision circuit disconnected or faulty
|  |  | 78 | #078: 15. cmd. supervision circuit disconnected or faulty
|  |  | 79 | #079: 16. cmd. supervision circuit disconnected or faulty
|  |  | 80 | #080: 17. cmd. supervision circuit disconnected or faulty
|  |  | 81 | #081: 18. cmd. supervision circuit disconnected or faulty
|  |  | 82 | #082: 19. cmd. supervision circuit disconnected or faulty
|  |  | 83 | #083: 20. cmd. supervision circuit disconnected or faulty
|  |  | 84 | #084: 21. cmd. supervision circuit disconnected or faulty
|  |  | 85 | #085: 22. cmd. supervision circuit disconnected or faulty
|  |  | 86 | #086: 23. cmd. supervision circuit disconnected or faulty
|  |  | 87 | #087: 24. cmd. supervision circuit disconnected or faulty
|  |  | 88 | #088: 25. cmd. supervision circuit disconnected or faulty
|  |  | 89 | #089: 26. cmd. supervision circuit disconnected or faulty
|  |  | 90 | #090: 27. cmd. supervision circuit disconnected or faulty
|  |  | 91 | #091: 28. cmd. supervision circuit disconnected or faulty
|  |  | 92 | #092: 29. cmd. supervision circuit disconnected or faulty
|  |  | 93 | #093: 30. cmd. supervision circuit disconnected or faulty
|  |  | 94 | #094: 31. cmd. supervision circuit disconnected or faulty
|  |  | 95 | #095: 32. cmd. supervision circuit disconnected or faulty
|  |  | 96 | #096: SNTP Client 1 synchronized
|  |  | 97 | #097: SNTP Client 2 synchronized
|  |  | 98 | #098
|  |  | 99 | #099
|  |  | 100 | #100: Local control authority active
|  |  | 101 | #101: Host 1 online
|  |  | 102 | #102: Host 2 online
|  |  | 103 | #103: Host 3 online
|  |  | 104 | #104: Host 4 online
|  |  | 105 | #105: Host 5 online
|  |  | 106 | #106: Host 6 online
|  |  | 107 | #107: Host 7 online
|  |  | 108 | #108: Host 8 online
|  |  | 109 | #109: Host 9 online
|  |  | 110 | #110: Host 10 online
|  |  | 111 | #111: Host 11 online
|  |  | 112 | #112: Host 12 online
|  |  | 113 | #113: Host 13 online
|  |  | 114 | #114: Host 14 online
|  |  | 115 | #115: Host 15 online
|  |  | 116 | #116: Host 16 online
|  |  | 117 | #117: Host communication interface 1: At least one change of information lost
|  |  | 118 | #118: Host communication interface 2: At least one change of information lost
|  |  | 119 | #119: Host communication interface 3: At least one change of information lost
|  |  | 120 | #120: Host communication interface 4: At least one change of information lost
|  |  | 121 | #121: Host communication interface 5: At least one change of information lost
|  |  | 122 | #122: Host communication interface 6: At least one change of information lost
|  |  | 123 | #123: Host communication interface 7: At least one change of information lost
|  |  | 124 | #124: Host communication interface 8: At least one change of information lost
|  |  | 125 | #125: Host communication interface 9: At least one change of information lost
|  |  | 126 | #126: Host communication interface 10: At least one change of information lost
|  |  | 127 | #127: Host communication interface 11: At least one change of information lost
|  |  | 128 | #128: Host communication interface 12: At least one change of information lost
|  |  | 129 | #129: Host communication interface 13: At least one change of information lost
|  |  | 130 | #130: Host communication interface 14: At least one change of information lost
|  |  | 131 | #131: Host communication interface 15: At least one change of information lost
|  |  | 132 | #132: Host communication interface 16: At least one change of information lost
|  |  | 133 | #133: Host communication interface 1: At least one pulse counter lost
|  |  | 134 | #134: Host communication interface 2: At least one pulse counter lost
|  |  | 135 | #135: Host communication interface 3: At least one pulse counter lost
|  |  | 136 | #136: Host communication interface 4: At least one pulse counter lost
|  |  | 137 | #137: Host communication interface 5: At least one pulse counter lost
|  |  | 138 | #138: Host communication interface 6: At least one pulse counter lost
|  |  | 139 | #139: Host communication interface 7: At least one pulse counter lost
|  |  | 140 | #140: Host communication interface 8: At least one pulse counter lost
|  |  | 141 | #141: Host communication interface 9: At least one pulse counter lost
|  |  | 142 | #142: Host communication interface 10: At least one pulse counter lost
|  |  | 143 | #143: Host communication interface 11: At least one pulse counter lost
|  |  | 144 | #144: Host communication interface 12: At least one pulse counter lost
|  |  | 145 | #145: Host communication interface 13: At least one pulse counter lost
|  |  | 146 | #146: Host communication interface 14: At least one pulse counter lost
|  |  | 147 | #147: Host communication interface 15: At least one pulse counter lost
|  |  | 148 | #148: Host communication interface 16: At least one pulse counter lost
|  |  | 149 | #149: CMU 1 operable
|  |  | 150 | #150: CMU 2 operable
|  |  | 151 | #151: CMU 3 operable
|  |  | 152 | #152: CMU 4 operable
|  |  | 153 | #153: CMU 5 operable
|  |  | 154 | #154: CMU 6 operable
|  |  | 155 | #155: CMU 7 operable
|  |  | 156 | #156: CMU 8 operable
|  |  | 157 | #157: CMU 9 operable
|  |  | 158 | #158: CMU 10 operable
|  |  | 159 | #159: CMU 11 operable
|  |  | 160 | #160: CMU 12 operable
|  |  | 161 | #161: CMU 13 operable
|  |  | 162 | #162: CMU 14 operable
|  |  | 163 | #163: CMU 15 operable
|  |  | 164 | #164: CMU 16 operable
|  |  | 165 | #165
|  |  | 166 | #166
|  |  | 167 | #167
|  |  | 168 | #168
|  |  | 169 | #169
|  |  | 170 | #170
|  |  | 171 | #171
|  |  | 172 | #172
|  |  | 173 | #173
|  |  | 174 | #174: Data base identity tag
|  |  | 175 | #175
|  |  | 176 | #176
|  |  | 177 | #177
|  |  | 178 | #178
|  |  | 179 | #179
|  |  | 180 | #180: Device reachable on redundant line 1
|  |  | 181 | #181: Device reachable on redundant line 2
|  |  | 182 | #182: Device reachable on redundant line 3
|  |  | 183 | #183: Device reachable on redundant line 4
|  |  | 184 | #184: Device active on redundant line 1
|  |  | 185 | #185: Device active on redundant line 2
|  |  | 186 | #186: Device active on redundant line 3
|  |  | 187 | #187: Device active on redundant line 4
|  |  | 188 | #188: Device preferred on redundant line 1
|  |  | 189 | #189: Device preferred on redundant line 2
|  |  | 190 | #190: Device preferred on redundant line 3
|  |  | 191 | #191: Device preferred on redundant line 4
|  |  | 192 | #192: Network element no. 1 operable
|  |  | 193 | #193: Network element no. 2 operable
|  |  | 194 | #194: Network element no. 3 operable
|  |  | 195 | #195: Network element no. 4 operable
|  |  | 196 | #196: Network element no. 5 operable
|  |  | 197 | #197: Network element no. 6 operable
|  |  | 198 | #198: Network element no. 7 operable
|  |  | 199 | #199: Network element no. 8 operable
|  |  | 200 | #200: Network element no. 9 operable
|  |  | 201 | #201: Network element no. 10 operable
|  |  | 202 | #202: Network element no. 11 operable
|  |  | 203 | #203: Network element no. 12 operable
|  |  | 204 | #204: Network element no. 13 operable
|  |  | 205 | #205: Network element no. 14 operable
|  |  | 206 | #206: Network element no. 15 operable
|  |  | 207 | #207: Network element no. 16 operable
|  |  | 208 | #208: Network element no. 17 operable
|  |  | 209 | #209: Network element no. 18 operable
|  |  | 210 | #210: Network element no. 19 operable
|  |  | 211 | #211: Network element no. 20 operable
|  |  | 212 | #212: Network element no. 21 operable
|  |  | 213 | #213: Network element no. 22 operable
|  |  | 214 | #214: Network element no. 23 operable
|  |  | 215 | #215: Network element no. 24 operable
|  |  | 216 | #216: Network element no. 25 operable
|  |  | 217 | #217: Network element no. 26 operable
|  |  | 218 | #218: Network element no. 27 operable
|  |  | 219 | #219: Network element no. 28 operable
|  |  | 220 | #220: Network element no. 29 operable
|  |  | 221 | #221: Network element no. 30 operable
|  |  | 222 | #222: Network element no. 31 operable
|  |  | 223 | #223: Network element no. 32 operable
|  |  | 224 | #224: CMU 1 active
|  |  | 225 | #225: CMU 2 active
|  |  | 226 | #226: CMU 3 active
|  |  | 227 | #227: CMU 4 active
|  |  | 228 | #228: CMU 5 active
|  |  | 229 | #229: CMU 6 active
|  |  | 230 | #230: CMU 7 active
|  |  | 231 | #231: CMU 8 active
|  |  | 232 | #232: CMU 9 active
|  |  | 233 | #233: CMU 10 active
|  |  | 234 | #234: CMU 11 active
|  |  | 235 | #235: CMU 12 active
|  |  | 236 | #236: CMU 13 active
|  |  | 237 | #237: CMU 14 active
|  |  | 238 | #238: CMU 15 active
|  |  | 239 | #239: CMU 16 active
|  |  | 240 | #240
|  |  | 241 | #241
|  |  | 242 | #242: Command collision with host 1
|  |  | 243 | #243: Command collision with host 2
|  |  | 244 | #244: Command collision with host 3
|  |  | 245 | #245: Command collision with host 4
|  |  | 246 | #246: Command collision with host 5
|  |  | 247 | #247: Command collision with host 6
|  |  | 248 | #248: Command collision with host 7
|  |  | 249 | #249: Command collision with host 8
|  |  | 250 | #250: Command collision with host 9
|  |  | 251 | #251: Command collision with host 10
|  |  | 252 | #252: Command collision with host 11
|  |  | 253 | #253: Command collision with host 12
|  |  | 254 | #254: Command collision with host 13
|  |  | 255 | #255: Command collision with host 14
|  |  | 256 | #256: Command collision with host 15
|  |  | 257 | #257: Command collision with host 16
|  |  | 258 | #258: Command collision with Integrated HMI
|  |  | 259 | #259: Command collision with web server
|  |  | 260 | #260: Command collision with PLC
|  |  | 261 | #261: Integrated HMI Client 1 online
|  |  | 262 | #262: Integrated HMI Client 2 online
|  |  | 263 | #263: Integrated HMI Client 3 online
|  |  | 264 | #264: Integrated HMI Client 4 online
|  |  | 265 | #265: Integrated HMI Client 5 online
|  |  | 266 | #266: Integrated HMI Client 6 online
|  |  | 267 | #267: Integrated HMI Client 7 online
|  |  | 268 | #268: Integrated HMI Client 8 online
|  |  | 269 | #269: Integrated HMI Client 9 online
|  |  | 270 | #270: Integrated HMI Client 10 online
|  |  | 271 | #271: Integrated HMI Client 11 online
|  |  | 272 | #272: Integrated HMI Client 12 online
|  |  | 273 | #273: Integrated HMI Client 13 online
|  |  | 274 | #274: Integrated HMI Client 14 online
|  |  | 275 | #275: Integrated HMI Client 15 online
|  |  | 276 | #276: Integrated HMI Client 16 online
|  |  | 277 | #277: PRP interface 1: Network interface E1 link on
|  |  | 278 | #278: PRP interface 2: Network interface E1 link on
|  |  | 279 | #279: PRP interface 3: Network interface E1 link on
|  |  | 280 | #280: PRP interface 4: Network interface E1 link on
|  |  | 281 | #281: PRP interface 5: Network interface E1 link on
|  |  | 282 | #282: PRP interface 6: Network interface E1 link on
|  |  | 283 | #283: PRP interface 7: Network interface E1 link on
|  |  | 284 | #284: PRP interface 8: Network interface E1 link on
|  |  | 285 | #285: PRP interface 1: Network interface E2 link on
|  |  | 286 | #286: PRP interface 2: Network interface E2 link on
|  |  | 287 | #287: PRP interface 3: Network interface E2 link on
|  |  | 288 | #288: PRP interface 4: Network interface E2 link on
|  |  | 289 | #289: PRP interface 5: Network interface E2 link on
|  |  | 290 | #290: PRP interface 6: Network interface E2 link on
|  |  | 291 | #291: PRP interface 7: Network interface E2 link on
|  |  | 292 | #292: PRP interface 8: Network interface E2 link on
|  |  | 293 | #293: Host communication interface 1: SOE buffer filling status is not reached
|  |  | 294 | #294: Host communication interface 2: SOE buffer filling status is not reached
|  |  | 295 | #295: Host communication interface 3: SOE buffer filling status is not reached
|  |  | 296 | #296: Host communication interface 4: SOE buffer filling status is not reached
|  |  | 297 | #297: Host communication interface 5: SOE buffer filling status is not reached
|  |  | 298 | #298: Host communication interface 6: SOE buffer filling status is not reached
|  |  | 299 | #299: Host communication interface 7: SOE buffer filling status is not reached
|  |  | 300 | #300: Host communication interface 8: SOE buffer filling status is not reached
|  |  | 301 | #301: Host communication interface 9: SOE buffer filling status is not reached
|  |  | 302 | #302: Host communication interface 10: SOE buffer filling status is not reached
|  |  | 303 | #303: Host communication interface 11: SOE buffer filling status is not reached
|  |  | 304 | #304: Host communication interface 12: SOE buffer filling status is not reached
|  |  | 305 | #305: Host communication interface 13: SOE buffer filling status is not reached
|  |  | 306 | #306: Host communication interface 14: SOE buffer filling status is not reached
|  |  | 307 | #307: Host communication interface 15: SOE buffer filling status is not reached
|  |  | 308 | #308: Host communication interface 16: SOE buffer filling status is not reached
|  |  | 309 | #309: CAM client 1 online
|  |  | 310 | #310: CAM client 2 online
|  |  | 311 | #311: CAM client 3 online
|  |  | 312 | #312: CAM client 4 online
|  |  | 313 | #313: RTC battery voltage low
|  |  | 10001 | #001: Put device out of service
|  |  | 10002 | #002: Reset device process
|  |  | 10003 | #003: Connect device
|  |  | 10004 | #004: Set redundant line 1 as preferred line
|  |  | 10005 | #005: Set redundant line 2 as preferred line
|  |  | 10006 | #006: Set redundant line 3 as preferred line
|  |  | 10007 | #007: Set redundant line 4 as preferred line
|  |  | 10008 | #008
|  |  | 10009 | #009
|  |  | 10010 | #010
|  |  | 10011 | #011
|  |  | 10012 | #012: Force global process image update
|  |  | 10013 | #013
|  |  | 10014 | #014
|  |  | 10015 | #015
|  |  | 10016 | #016: Switch over to redundant CMU 1
|  |  | 10017 | #017: Switch over to redundant CMU 2
|  |  | 10018 | #018: Switch over to redundant CMU 3
|  |  | 10019 | #019: Switch over to redundant CMU 4
|  |  | 10020 | #020: Switch over to redundant CMU 5
|  |  | 10021 | #021: Switch over to redundant CMU 6
|  |  | 10022 | #022: Switch over to redundant CMU 7
|  |  | 10023 | #023: Switch over to redundant CMU 8
|  |  | 10024 | #024: Switch over to redundant CMU 9
|  |  | 10025 | #025: Switch over to redundant CMU 10
|  |  | 10026 | #026: Switch over to redundant CMU 11
|  |  | 10027 | #027: Switch over to redundant CMU 12
|  |  | 10028 | #028: Switch over to redundant CMU 13
|  |  | 10029 | #029: Switch over to redundant CMU 14
|  |  | 10030 | #030: Switch over to redundant CMU 15
|  |  | 10031 | #031: Switch over to redundant CMU 16
ThresholdSupervisionTypes |  |  | 16143 | Integrated
|  |  | 16144 | Absolute
VALUE_FORMAT |  |  | 16611 | Double bit indication
|  |  | 16612 | Double bit indication reversed
|  |  | 16613 | Single bit indication
|  |  | 16614 | Single bit indication reversed
|  |  | 16579 | 16 bit unsigned integer value
|  |  | 16607 | 16 bit signed integer value
|  |  | 16580 | 32 bit unsigned integer (high word in first register)
|  |  | 16581 | 32 bit signed integer (high word in first register)
|  |  | 16594 | 32 bit unsigned integer (high word in second register)
|  |  | 16595 | 32 bit signed integer (high word in second register)
|  |  | 16592 | 32 bit binary value (high word in first register)
|  |  | 16593 | 32 bit binary value (high word in second register)
|  |  | 16587 | 32 bit floating point value (high word in first register)
|  |  | 16588 | 32 bit floating point value (high word in second register)
|  |  | 16589 | 16 bit scaled value
|  |  | 16590 | 32 bit scaled value (high word in first register)
|  |  | 16591 | 32 bit scaled value (high word in second register)
|  |  | 16730 | 16 bit unsigned scaled value
|  |  | 16731 | 32 bit unsigned scaled value (high word in first register)
|  |  | 16732 | 32 bit unsigned scaled value (high word in second register)
YesNo_01 |  |  | 1 | Y
|  |  | 0 | N
_End

## CP03
_EndColumn
Signal type | System data type | Type variant (AMI and EPI) | 1 of n control group (ASO, BSO, DCO, DSO, FSO, RCO, SCO, TDC) | Control authority group (ASO, BSO, DCO, DSO, FSO, RCO, SCO, TDC) | Alarm for intermediate position (DPI) | Alarm for OFF position (DPI, SPI) | Alarm for ON position (DPI, SPI) | Alarm for indeterminate position (DPI) | Monitoring data blocking group (Input only) | Scaled values (AMI/DMI/ASO/DSO) | Maximum value (100%) (AMI/DMI/ASO/DSO) | Minimum value (-100%) (AMI/DMI/ASO/DSO) | Engineering unit (AMI/DMI/ASO/DSO/FSO/MFI) | RTUtil500 import | Export status | STA | BAY | DEV | SCADA object | Intelligent electronic device (IED) name | File Type (FTR and FDR) | Directory | Num. of archived files in dir. | Time of storage in directory | Dir. search pattern | Directory path | Time interval | Max. info elements | Slave address | Function code | Index | Index for "off" / "lower" (DCO, RCO, SCO) | Query range | Bit position | Threshold supervision (AMI, MFI) | Threshold supervision type (AMI, MFI) | Threshold value (AMI, MFI) | Maximum value (DMI, DSO) | Event handling enabled (DPI, SPI) | Code number (SPI) | Channel number (DPI, SPI) | Event number state "on" (DPI, SPI) | Event number state "off" (DPI, SPI) | Event number state "intermediate" (DPI) | Event number state "indeterminate" (DPI) | Scaling limit mapping (AMI, ASO, DMI) | Value format (AMI, ASO, BSI32, DPI, FSO, ITI, MFI) | Minimum value (AMI, ASO, FSO, MFI) | Maximum value (AMI, ASO, FSO, MFI) | Minimum float value (AMI, ASO, FSO, MFI) | Maximum float value (AMI, ASO, FSO, MFI) | Confirm command on transmission (Commands and TDC) | ASDU address | Information object | Priority (SPI, DPI, DMI, EPI, STI) | Transmit with timestamp | In use | Spontaneous transmission (AMI, ITI, MFI) | Background cycle (AMI, MFI) | Transmission format (AMI, ASO, DSO) | Maximum value (100%) (AMI, ASO, DSO) | Minimum value (-100%) (AMI) | Interrogation group number (AMI, BSI, DMI, DPI, EPI, MFI, SEV, SPI, STI) | Include in sequence of event file (AMI, BSI, DMI, DPI, EPI, ITI, MFI, SEV, SPI, STI) | Max. contained ASDUs (FTR type 'Seq. of events') | Sections per file (FTR type 'Seq. of events') | Store in buffer (AMI, BSI, DMI, DPI, ITI, MFI, SEV, SPI, STI) | Update event filter (DPI, SPI)
Signal | [15 empty] | Process Object Identification |  |  |  | IED / SDISub name | FTR | [7 empty] | CP03 (Modbus)-Sub Parameter | [23 empty] | SCADA (IEC 60870-5-104)-Address |  | SCADA (IEC 60870-5-104)-Host Parameter
5 ASCII | 4 ASCII | ASCII | 1 .. 200 | 1 .. 200 | Y / N | Y / N | Y / N | Y / N | 1 .. 200 | Y / N | -3.4E+38 .. 3.4E+38 | -3.4E+38 .. 3.4E+38 | 32 ASCII | Y / N | Added / Modified / Deleted | 12 ASCII | 12 ASCII | 45 ASCII | 59 ASCII | ASCII | Value from list | ASCII | 1 .. 255 | 1 .. 365 | ASCII | ASCII | 1 .. 918000 | 1 .. 3600 | 0 .. 255 | 1-7, 15, 16 | 0 .. 65535 | 0 .. 65535 | 1 .. 32 | 0 .. 15 | Y / N | Integrated, absolute | AMI: 0..100%, MFI: 0,0..3.4E+38 | DMI16: -32768 ... +32767, DSO16: 0 .... +32767, DMI08: -128 .... +127, DSO08: 0 ... 127 | Y / N | 0 .. 67 | 0 .. 999 | 0 .. 255 | 0 .. 255 | 0 .. 255 | 0 .. 255 | Unipolar / Bipolar | ASCII (choose from list) | Depending on "value format" | Depending on "value format" | -3.4E+38 .. 3.4E+38 | -3.4E+38 .. 3.4E+38 | Y / N | 0 .. 65535 | 0 .. 16777215 | 1 / 2 | Y / N | Y / N | Y / N | Off, 1, 2, 4, 5, 8, 10, 16, 30, 60 sec, 2, 5, 10 min | Normalized, Scaled | -32768 .. 32767 | -32768 .. 32767 | 1 .. 16 | Y / N | 1 ... 5000 | 1 ... 100 | Y / N | 1 .. 300
STTY | STDT | STTV | COGR | COAU | ALINT | ALOFF | ALON | ALIND | MBGR | SCVEN | SCVMA | SCVMI | SCVEU | STIM | STATUS | OI01 | OI02 | OI03 | OI04 | IEDN | FTTY | FDR | FDDS | FDAD | FDSP | FDDP | FDTI | FDMX | T1SA | T1FC | T1IX | T1IOFF | T1QR | T1BP | T1THS | T1THY | T1THV | T1MXV | T1EVE | T1EVCO | T1EVCH | T1EVON | T1EVOF | T1EVIN | T1EVID | T1MSV | T1FO | T1MINRV | T1MAXRV | T1MINFV | T1MAXFV | T1CCT | E101 | E102 | E1PR | E1TI | E1IU | E1SP | E1BG | E1TF | E1MV | E1MNV | E1IGN | E1SEF | E1SOEMC | E1SOESP | E1PUB | E1UEF
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС24 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 23 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20024 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС23 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 22 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20023 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС22 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 21 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20022 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС21 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 20 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20021 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС20 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 19 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20020 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС19 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 18 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20019 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС18 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 17 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20018 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС17 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 16 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20017 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС16 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 15 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20016 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС15 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 14 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20015 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС14 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 13 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20014 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС13 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 12 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20013 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС12 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 11 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20012 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС11 Перегруз Т-1 | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 10 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20011 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС10 Перегруз Т-2 | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 9 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20010 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС09 Попередження | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 8 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20009 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС08 Аварія | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 7 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20008 | 2 | N | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС07 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 6 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20007 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС06 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 5 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20006 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС05 Резерв | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 4 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20005 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС04 АВ в шафі ТМ вимкнено | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20004 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС03 Двері КП (шафи ТМ) | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20003 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС02 Ключ М0/Д1 ПС Озерна | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20002 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3 Addr1 | AkonTC24 | ТС01 Живлення КП (шафи ТМ) | CP3 Addr1 шафа ТМ | [8 empty] | 1 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20001 | 2 | Y | Y | [6 empty] | N |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP3Addr31 | Akon 314 | ТВ02 | CP3Addr31 ВД-110 кВ Т-1 | [8 empty] | 31 | 3 | 16386 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 43104 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP3Addr31 | Akon 314 | ТВ01 | CP3Addr31 ВД-110 кВ Т-1 | [8 empty] | 31 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 43103 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr31 | Akon 314 | 04 | CP3Addr31 ВД-110 кВ Т-1 | [8 empty] | 31 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23105 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr31 | Akon 314 | 03 | CP3Addr31 ВД-110 кВ Т-1 | [8 empty] | 31 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23104 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr31 | Akon 314 | 02 | CP3Addr31 ВД-110 кВ Т-1 | [8 empty] | 31 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23102 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr31 | Akon 314 | 01 | CP3Addr31 ВД-110 кВ Т-1 | [8 empty] | 31 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23101 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozirna | CP3Addr31 | Akon 314 | ТК01 | CP3Addr31 ВД-110 кВ Т-1 | [8 empty] | 31 | 5 | 0 | 0 | 1 | [18 empty] | N | 1 | 13101 |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP3Addr32 | Akon 310 | ТВ01 | CP3Addr32 ВД-110 кВ Т-2 | [8 empty] | 32 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 43203 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP3Addr32 | Akon 310 | ТВ02 | CP3Addr32 ВД-110 кВ Т-2 | [8 empty] | 32 | 3 | 16386 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 43204 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SCO | [13 empty] | Y | added | Ozirna | CP3Addr32 | Akon 310 | ТК01 | CP3Addr32 ВД-110 кВ Т-2 | [8 empty] | 32 | 5 | 0 | 0 | 1 | [18 empty] | N | 1 | 13201 |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr32 | Akon 310 | 01 | CP3Addr32 ВД-110 кВ Т-2 | [8 empty] | 32 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23201 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr32 | Akon 310 | 02 | CP3Addr32 ВД-110 кВ Т-2 | [8 empty] | 32 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23202 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr32 | Akon 310 | 03 | CP3Addr32 ВД-110 кВ Т-2 | [8 empty] | 32 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23204 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr32 | Akon 310 | 04 | CP3Addr32 ВД-110 кВ Т-2 | [8 empty] | 32 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23205 | 2 | Y | Y | [6 empty] | N |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP3Addr33 | Akon 314 | ТВ02 | CP3Addr33 CВ-110 кВ | [8 empty] | 33 | 3 | 16386 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 43304 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP3Addr33 | Akon 314 | ТВ01 | CP3Addr33 CВ-110 кВ | [8 empty] | 33 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 43303 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr33 | Akon 314 | 04 | CP3Addr33 CВ-110 кВ | [8 empty] | 33 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23305 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr33 | Akon 314 | 03 | CP3Addr33 CВ-110 кВ | [8 empty] | 33 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23304 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr33 | Akon 314 | 02 | CP3Addr33 CВ-110 кВ | [8 empty] | 33 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23302 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr33 | Akon 314 | 01 | CP3Addr33 CВ-110 кВ | [8 empty] | 33 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23301 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozirna | CP3Addr33 | Akon 314 | ТК01 | CP3Addr33 CВ-110 кВ | [8 empty] | 33 | 5 | 0 | 0 | 1 | [18 empty] | N | 1 | 13301 |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP3Addr34 | Akon 314 | ТВ01 | CP3Addr34 CВ-110 кВ | [8 empty] | 34 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 43403 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP3Addr34 | Akon 314 | ТВ02 | CP3Addr34 CВ-110 кВ | [8 empty] | 34 | 3 | 16386 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 43404 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SCO | [13 empty] | Y | added | Ozirna | CP3Addr34 | Akon 314 | ТК01 | CP3Addr34 CВ-110 кВ | [8 empty] | 34 | 5 | 0 | 0 | 1 | [18 empty] | N | 1 | 13401 |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr34 | Akon 314 | 01 | CP3Addr34 CВ-110 кВ | [8 empty] | 34 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23401 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr34 | Akon 314 | 02 | CP3Addr34 CВ-110 кВ | [8 empty] | 34 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23402 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr34 | Akon 314 | 03 | CP3Addr34 CВ-110 кВ | [8 empty] | 34 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23404 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP3Addr34 | Akon 314 | 04 | CP3Addr34 CВ-110 кВ | [8 empty] | 34 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 23405 | 2 | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP3 Addr1 шафа ТМ | [32 empty] | 1 | 20000 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP3Addr31 ВД-110 кВ Т-1 | [32 empty] | 1 | 53101 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP3Addr32 ВД-110 кВ Т-2 | [32 empty] | 1 | 53201 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP3Addr33 CВ-110 кВ | [32 empty] | 1 | 53301 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP3Addr34 CВ-110 кВ | [32 empty] | 1 | 53401 |  | Y | Y | [6 empty] | N |  |  | Y
_End

## CP02
_EndColumn
Signal type | System data type | Type variant (AMI and EPI) | 1 of n control group (ASO, BSO, DCO, DSO, FSO, RCO, SCO, TDC) | Control authority group (ASO, BSO, DCO, DSO, FSO, RCO, SCO, TDC) | Alarm for intermediate position (DPI) | Alarm for OFF position (DPI, SPI) | Alarm for ON position (DPI, SPI) | Alarm for indeterminate position (DPI) | Monitoring data blocking group (Input only) | Scaled values (AMI/DMI/ASO/DSO) | Maximum value (100%) (AMI/DMI/ASO/DSO) | Minimum value (-100%) (AMI/DMI/ASO/DSO) | Engineering unit (AMI/DMI/ASO/DSO/FSO/MFI) | RTUtil500 import | Export status | STA | BAY | DEV | SCADA object | Intelligent electronic device (IED) name | File Type (FTR and FDR) | Directory | Num. of archived files in dir. | Time of storage in directory | Dir. search pattern | Directory path | Time interval | Max. info elements | Slave address | Function code | Index | Index for "off" / "lower" (DCO, RCO, SCO) | Query range | Bit position | Threshold supervision (AMI, MFI) | Threshold supervision type (AMI, MFI) | Threshold value (AMI, MFI) | Maximum value (DMI, DSO) | Event handling enabled (DPI, SPI) | Code number (SPI) | Channel number (DPI, SPI) | Event number state "on" (DPI, SPI) | Event number state "off" (DPI, SPI) | Event number state "intermediate" (DPI) | Event number state "indeterminate" (DPI) | Scaling limit mapping (AMI, ASO, DMI) | Value format (AMI, ASO, BSI32, DPI, FSO, ITI, MFI) | Minimum value (AMI, ASO, FSO, MFI) | Maximum value (AMI, ASO, FSO, MFI) | Minimum float value (AMI, ASO, FSO, MFI) | Maximum float value (AMI, ASO, FSO, MFI) | ASDU address | Information object | Priority (SPI, DPI, DMI, EPI, STI) | Transmit with timestamp | In use | Spontaneous transmission (AMI, ITI, MFI) | Background cycle (AMI, MFI) | Transmission format (AMI, ASO, DSO) | Maximum value (100%) (AMI, ASO, DSO) | Minimum value (-100%) (AMI) | Interrogation group number (AMI, BSI, DMI, DPI, EPI, MFI, SEV, SPI, STI) | Include in sequence of event file (AMI, BSI, DMI, DPI, EPI, ITI, MFI, SEV, SPI, STI) | Max. contained ASDUs (FTR type 'Seq. of events') | Sections per file (FTR type 'Seq. of events') | Store in buffer (AMI, BSI, DMI, DPI, ITI, MFI, SEV, SPI, STI) | Update event filter (DPI, SPI)
Signal | [15 empty] | Process Object Identification |  |  |  | IED / SDISub name | FTR | [7 empty] | CP02 (Modbus)-Sub Parameter | [22 empty] | ScadaE1 (IEC 60870-5-104)-Address |  | ScadaE1 (IEC 60870-5-104)-Host Parameter
5 ASCII | 4 ASCII | ASCII | 1 .. 200 | 1 .. 200 | Y / N | Y / N | Y / N | Y / N | 1 .. 200 | Y / N | -3.4E+38 .. 3.4E+38 | -3.4E+38 .. 3.4E+38 | 32 ASCII | Y / N | Added / Modified / Deleted | 10 ASCII | 10 ASCII | 10 ASCII | 26 ASCII | ASCII | Value from list | ASCII | 1 .. 255 | 1 .. 365 | ASCII | ASCII | 1 .. 918000 | 1 .. 3600 | 0 .. 255 | 1-7, 15, 16 | 0 .. 65535 | 0 .. 65535 | 1 .. 32 | 0 .. 15 | Y / N | Integrated, absolute | AMI: 0..100%, MFI: 0,0..3.4E+38 | DMI16: -32768 ... +32767, DSO16: 0 .... +32767, DMI08: -128 .... +127, DSO08: 0 ... 127 | Y / N | 0 .. 67 | 0 .. 999 | 0 .. 255 | 0 .. 255 | 0 .. 255 | 0 .. 255 | Unipolar / Bipolar | ASCII (choose from list) | Depending on "value format" | Depending on "value format" | -3.4E+38 .. 3.4E+38 | -3.4E+38 .. 3.4E+38 | 0 .. 65535 | 0 .. 16777215 | 1 / 2 | Y / N | Y / N | Y / N | Off, 1, 2, 4, 5, 8, 10, 16, 30, 60 sec, 2, 5, 10 min | Normalized, Scaled | -32768 .. 32767 | -32768 .. 32767 | 1 .. 16 | Y / N | 1 ... 5000 | 1 ... 100 | Y / N | 1 .. 300
STTY | STDT | STTV | COGR | COAU | ALINT | ALOFF | ALON | ALIND | MBGR | SCVEN | SCVMA | SCVMI | SCVEU | STIM | STATUS | OI01 | OI02 | OI03 | OI04 | IEDN | FTTY | FDR | FDDS | FDAD | FDSP | FDDP | FDTI | FDMX | T1SA | T1FC | T1IX | T1IOFF | T1QR | T1BP | T1THS | T1THY | T1THV | T1MXV | T1EVE | T1EVCO | T1EVCH | T1EVON | T1EVOF | T1EVIN | T1EVID | T1MSV | T1FO | T1MINRV | T1MAXRV | T1MINFV | T1MAXFV | E101 | E102 | E1PR | E1TI | E1IU | E1SP | E1BG | E1TF | E1MV | E1MNV | E1IGN | E1SEF | E1SOEMC | E1SOESP | E1PUB | E1UEF
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr10 | Akon 310 | ТС04 Резерв к10 Бакали | CP2 Addr10 В-10 кВ "Бакали" | [8 empty] | 10 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21005 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr10 | Akon 310 | ТС03 Резерв к10 Бакали | CP2 Addr10 В-10 кВ "Бакали" | [8 empty] | 10 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21004 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr10 | Akon 310 | ТС02Полож к10 10 кВ Бакали | CP2 Addr10 В-10 кВ "Бакали" | [8 empty] | 10 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21002 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr10 | Akon 310 | ТС01 М(0)/Д(1) к10 Бакали | CP2 Addr10 В-10 кВ "Бакали" | [8 empty] | 10 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21001 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozerna | CP2 Addr10 | Akon 310 | ТК01 ком. 10 В-10 Бакали | CP2 Addr10 В-10 кВ "Бакали" | [8 empty] | 10 | 5 | 0 | 0 | 1 | [18 empty] | 1 | 11001 |  |  | Y
MFI | [13 empty] | Y | added | Ozerna | CP2 Addr10 | Akon 310 | ТВ01 Ia к 10 Бакали | CP2 Addr10 В-10 кВ "Бакали" | [8 empty] | 10 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 | 1 | 41003 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr08 | Akon 310 | ТС01 М(0)/Д(1) к8 СВ-10 | CP2 Addr08 В-10 кВ СВ-10 | [8 empty] | 8 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 20801 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr08 | Akon 310 | ТС02 Полож к8 В-10 кВ СВ10 | CP2 Addr08 В-10 кВ СВ-10 | [8 empty] | 8 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 20802 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozerna | CP2 Addr08 | Akon 310 | ТК01 Керув к8 В-10 кВ СВ10 | CP2 Addr08 В-10 кВ СВ-10 | [8 empty] | 8 | 5 | 0 | 0 | 1 | [18 empty] | 1 | 10801 |  |  | Y
MFI | [13 empty] | Y | added | Ozerna | CP2 Addr08 | Akon 310 | ТВ01 Ia к8 В-10 кВ СВ-10 | CP2 Addr08 В-10 кВ СВ-10 | [8 empty] | 8 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 | 1 | 40803 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr08 | Akon 310 | ТС03 контроль ШУ | CP2 Addr08 В-10 кВ СВ-10 | [8 empty] | 8 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 20804 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr08 | Akon 310 | ТС04Резерв к8 В-10 кВ СВ10 | CP2 Addr08 В-10 кВ СВ-10 | [8 empty] | 8 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 20805 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr12 | Akon 310 | ТС04 "Земля" в мережі 2сш. | CP2 Addr12 В-10 кВ "Щербаки" | [8 empty] | 12 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21205 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr12 | Akon 310 | ТС03 Несправність ТН-10-2 | CP2 Addr12 В-10 кВ "Щербаки" | [8 empty] | 12 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21204 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr12 | Akon 310 | ТС02 Полож к12 Щербаки | CP2 Addr12 В-10 кВ "Щербаки" | [8 empty] | 12 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21202 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr12 | Akon 310 | ТС01 М(0)/Д(1) к12 Щербаки | CP2 Addr12 В-10 кВ "Щербаки" | [8 empty] | 12 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21201 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozerna | CP2 Addr12 | Akon 310 | ТК01 Керув. к.12 Щербаки | CP2 Addr12 В-10 кВ "Щербаки" | [8 empty] | 12 | 5 | 0 | 0 | 1 | [18 empty] | 1 | 11201 |  |  | Y
MFI | [13 empty] | Y | added | Ozerna | CP2 Addr12 | Akon 310 | ТВ01 Ia к12 Щербаки | CP2 Addr12 В-10 кВ "Щербаки" | [8 empty] | 12 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 | 1 | 41203 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr16 | Akon 310 | ТС04 Резерв к.14 Т-2 | CP2 Addr16 В-10 кВ Т-2 | [8 empty] | 16 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21605 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr16 | Akon 310 | ТС03 Резерв к.14 Т-2 | CP2 Addr16 В-10 кВ Т-2 | [8 empty] | 16 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21604 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr16 | Akon 310 | ТС02 Полож. к.14 Т-2 | CP2 Addr16 В-10 кВ Т-2 | [8 empty] | 16 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21602 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr16 | Akon 310 | ТС01 М(0)/Д(1) ком.14 Т2 | CP2 Addr16 В-10 кВ Т-2 | [8 empty] | 16 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21601 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozerna | CP2 Addr16 | Akon 310 | ТК01 Керув. к14 В-10 кВ Т2 | CP2 Addr16 В-10 кВ Т-2 | [8 empty] | 16 | 5 | 0 | 0 | 1 | [18 empty] | 1 | 11601 |  |  | Y
MFI | [13 empty] | Y | added | Ozerna | CP2 Addr16 | Akon 310 | ТВ02 UАB 2 сш.10кВ | CP2 Addr16 В-10 кВ Т-2 | [8 empty] | 16 | 3 | 16386 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 | 1 | 41604 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
MFI | [13 empty] | Y | added | Ozerna | CP2 Addr16 | Akon 310 | ТВ01 Ia к14 В-10 кВ Т-2 | CP2 Addr16 В-10 кВ Т-2 | [8 empty] | 16 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 | 1 | 41603 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr11 | Akon 310 | ТС04 Резерв ком.11 РП1 | CP2 Addr11 В-10 кВ "РП -1" | [8 empty] | 11 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21105 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr11 | Akon 310 | ТС03 Резерв ком.11 РП1 | CP2 Addr11 В-10 кВ "РП -1" | [8 empty] | 11 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21104 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr11 | Akon 310 | ТС02 Полож к.11 В10 кВ РП1 | CP2 Addr11 В-10 кВ "РП -1" | [8 empty] | 11 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21102 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr11 | Akon 310 | ТС01 М(0)/Д(1) к11 РП 1 | CP2 Addr11 В-10 кВ "РП -1" | [8 empty] | 11 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 21101 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozerna | CP2 Addr11 | Akon 310 | ТК01Керув ком11 В10 кВ РП1 | CP2 Addr11 В-10 кВ "РП -1" | [8 empty] | 11 | 5 | 0 | 0 | 1 | [18 empty] | 1 | 11101 |  |  | Y
MFI | [13 empty] | Y | added | Ozerna | CP2 Addr11 | Akon 310 | ТВ01 Ia к.11 В-10 кВ РП 1 | CP2 Addr11 В-10 кВ "РП -1" | [8 empty] | 11 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 | 1 | 41103 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr07 | Akon 310 | ТС01 М(0)/Д(1) к7Сільгосп. | CP2 Addr07 В-10 кВ "Сільгосп. Тех." | [8 empty] | 7 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 20701 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr07 | Akon 310 | ТС02 Полож к7Сільгосп. Тех | CP2 Addr07 В-10 кВ "Сільгосп. Тех." | [8 empty] | 7 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 20702 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozerna | CP2 Addr07 | Akon 310 | ТК01 Керув к7Сільгосп. Тех | CP2 Addr07 В-10 кВ "Сільгосп. Тех." | [8 empty] | 7 | 5 | 0 | 0 | 1 | [18 empty] | 1 | 10701 |  |  | Y
MFI | [13 empty] | Y | added | Ozerna | CP2 Addr07 | Akon 310 | ТВ01 Ia к7 Сільгосп. Тех. | CP2 Addr07 В-10 кВ "Сільгосп. Тех." | [8 empty] | 7 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 | 1 | 40703 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr07 | Akon 310 | ТС03Резерв к7Сільгосп. Тех | CP2 Addr07 В-10 кВ "Сільгосп. Тех." | [8 empty] | 7 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 20704 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozerna | CP2 Addr07 | Akon 310 | ТС04Резерв к7Сільгосп. Тех | CP2 Addr07 В-10 кВ "Сільгосп. Тех." | [8 empty] | 7 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [8 empty] | 1 | 20705 | 2 | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP2 Addr10 В-10 кВ "Бакали" | [31 empty] | 1 | 51001 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP2 Addr08 В-10 кВ СВ-10 | [31 empty] | 1 | 50801 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP2 Addr12 В-10 кВ "Щербаки" | [31 empty] | 1 | 51201 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP2 Addr16 В-10 кВ Т-2 | [31 empty] | 1 | 51601 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP2 Addr11 В-10 кВ "РП -1" | [31 empty] | 1 | 51101 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP2 Addr07 В-10 кВ "Сільгосп. Тех." | [31 empty] | 1 | 50701 |  | Y | Y | [6 empty] | N |  |  | Y
_End

## CP01
_EndColumn
Signal type | System data type | Type variant (AMI and EPI) | 1 of n control group (ASO, BSO, DCO, DSO, FSO, RCO, SCO, TDC) | Control authority group (ASO, BSO, DCO, DSO, FSO, RCO, SCO, TDC) | Alarm for intermediate position (DPI) | Alarm for OFF position (DPI, SPI) | Alarm for ON position (DPI, SPI) | Alarm for indeterminate position (DPI) | Monitoring data blocking group (Input only) | Scaled values (AMI/DMI/ASO/DSO) | Maximum value (100%) (AMI/DMI/ASO/DSO) | Minimum value (-100%) (AMI/DMI/ASO/DSO) | Engineering unit (AMI/DMI/ASO/DSO/FSO/MFI) | RTUtil500 import | Export status | STA | BAY | DEV | SCADA object | Intelligent electronic device (IED) name | File Type (FTR and FDR) | Directory | Num. of archived files in dir. | Time of storage in directory | Dir. search pattern | Directory path | Time interval | Max. info elements | Slave address | Function code | Index | Index for "off" / "lower" (DCO, RCO, SCO) | Query range | Bit position | Threshold supervision (AMI, MFI) | Threshold supervision type (AMI, MFI) | Threshold value (AMI, MFI) | Maximum value (DMI, DSO) | Event handling enabled (DPI, SPI) | Code number (SPI) | Channel number (DPI, SPI) | Event number state "on" (DPI, SPI) | Event number state "off" (DPI, SPI) | Event number state "intermediate" (DPI) | Event number state "indeterminate" (DPI) | Scaling limit mapping (AMI, ASO, DMI) | Value format (AMI, ASO, BSI32, DPI, FSO, ITI, MFI) | Minimum value (AMI, ASO, FSO, MFI) | Maximum value (AMI, ASO, FSO, MFI) | Minimum float value (AMI, ASO, FSO, MFI) | Maximum float value (AMI, ASO, FSO, MFI) | Confirm command on transmission (Commands and TDC) | ASDU address | Information object | Priority (SPI, DPI, DMI, EPI, STI) | Transmit with timestamp | In use | Spontaneous transmission (AMI, ITI, MFI) | Background cycle (AMI, MFI) | Transmission format (AMI, ASO, DSO) | Maximum value (100%) (AMI, ASO, DSO) | Minimum value (-100%) (AMI) | Interrogation group number (AMI, BSI, DMI, DPI, EPI, MFI, SEV, SPI, STI) | Include in sequence of event file (AMI, BSI, DMI, DPI, EPI, ITI, MFI, SEV, SPI, STI) | Max. contained ASDUs (FTR type 'Seq. of events') | Sections per file (FTR type 'Seq. of events') | Store in buffer (AMI, BSI, DMI, DPI, ITI, MFI, SEV, SPI, STI) | Update event filter (DPI, SPI)
Signal | [15 empty] | Process Object Identification |  |  |  | IED / SDISub name | FTR | [7 empty] | CP01 (Modbus)-Sub Parameter | [23 empty] | SCADA (IEC 60870-5-104)-Address |  | SCADA (IEC 60870-5-104)-Host Parameter
5 ASCII | 4 ASCII | ASCII | 1 .. 200 | 1 .. 200 | Y / N | Y / N | Y / N | Y / N | 1 .. 200 | Y / N | -3.4E+38 .. 3.4E+38 | -3.4E+38 .. 3.4E+38 | 32 ASCII | Y / N | Added / Modified / Deleted | 12 ASCII | 12 ASCII | 45 ASCII | 59 ASCII | ASCII | Value from list | ASCII | 1 .. 255 | 1 .. 365 | ASCII | ASCII | 1 .. 918000 | 1 .. 3600 | 0 .. 255 | 1-7, 15, 16 | 0 .. 65535 | 0 .. 65535 | 1 .. 32 | 0 .. 15 | Y / N | Integrated, absolute | AMI: 0..100%, MFI: 0,0..3.4E+38 | DMI16: -32768 ... +32767, DSO16: 0 .... +32767, DMI08: -128 .... +127, DSO08: 0 ... 127 | Y / N | 0 .. 67 | 0 .. 999 | 0 .. 255 | 0 .. 255 | 0 .. 255 | 0 .. 255 | Unipolar / Bipolar | ASCII (choose from list) | Depending on "value format" | Depending on "value format" | -3.4E+38 .. 3.4E+38 | -3.4E+38 .. 3.4E+38 | Y / N | 0 .. 65535 | 0 .. 16777215 | 1 / 2 | Y / N | Y / N | Y / N | Off, 1, 2, 4, 5, 8, 10, 16, 30, 60 sec, 2, 5, 10 min | Normalized, Scaled | -32768 .. 32767 | -32768 .. 32767 | 1 .. 16 | Y / N | 1 ... 5000 | 1 ... 100 | Y / N | 1 .. 300
STTY | STDT | STTV | COGR | COAU | ALINT | ALOFF | ALON | ALIND | MBGR | SCVEN | SCVMA | SCVMI | SCVEU | STIM | STATUS | OI01 | OI02 | OI03 | OI04 | IEDN | FTTY | FDR | FDDS | FDAD | FDSP | FDDP | FDTI | FDMX | T1SA | T1FC | T1IX | T1IOFF | T1QR | T1BP | T1THS | T1THY | T1THV | T1MXV | T1EVE | T1EVCO | T1EVCH | T1EVON | T1EVOF | T1EVIN | T1EVID | T1MSV | T1FO | T1MINRV | T1MAXRV | T1MINFV | T1MAXFV | T1CCT | E101 | E102 | E1PR | E1TI | E1IU | E1SP | E1BG | E1TF | E1MV | E1MNV | E1IGN | E1SEF | E1SOEMC | E1SOESP | E1PUB | E1UEF
MFI | [13 empty] | Y | added | Ozirna | CP1 Addr1k | Akon 310 | ТВ01 Ia к1 10 кВ Резерв | CP1 Addr1 10 кВ "Резерв" | [8 empty] | 1 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 40103 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr1k | Akon 310 | 04 | CP1 Addr1 10 кВ "Резерв" | [8 empty] | 1 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20105 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr1k | Akon 310 | 03 | CP1 Addr1 10 кВ "Резерв" | [8 empty] | 1 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20104 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr1k | Akon 310 | 02 | CP1 Addr1 10 кВ "Резерв" | [8 empty] | 1 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20102 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr1k | Akon 310 | 01 | CP1 Addr1 10 кВ "Резерв" | [8 empty] | 1 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20101 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozirna | CP1 Addr1k | Akon 310 | ТК01 к1 10 кВ "Резерв" | CP1 Addr1 10 кВ "Резерв" | [8 empty] | 1 | 5 | 0 | 0 | 1 | [18 empty] | N | 1 | 10101 |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP1 Addr2k | Akon 310 | ТВ01 | CP1 Addr2 В-10 кВ "Межовий" | [8 empty] | 2 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 40203 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr2k | Akon 310 | 04 | CP1 Addr2 В-10 кВ "Межовий" | [8 empty] | 2 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20205 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr2k | Akon 310 | 03 | CP1 Addr2 В-10 кВ "Межовий" | [8 empty] | 2 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20204 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr2k | Akon 310 | 02 | CP1 Addr2 В-10 кВ "Межовий" | [8 empty] | 2 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20202 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr2k | Akon 310 | 01 | CP1 Addr2 В-10 кВ "Межовий" | [8 empty] | 2 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20201 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozirna | CP1 Addr2k | Akon 310 | ТК01 | CP1 Addr2 В-10 кВ "Межовий" | [8 empty] | 2 | 5 | 0 | 0 | 1 | [18 empty] | N | 1 | 10201 |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP1 Addr3k | Akon 314 | ТВ02 UАB 1 сш. 10 кВ к3 Т1 | CP1 Addr3 В-10 кВ Т-1 | [8 empty] | 3 | 3 | 16386 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 40304 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP1 Addr3k | Akon 314 | ТВ01 | CP1 Addr3 В-10 кВ Т-1 | [8 empty] | 3 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 40303 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr3k | Akon 314 | 04 | CP1 Addr3 В-10 кВ Т-1 | [8 empty] | 3 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20305 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr3k | Akon 314 | 03 | CP1 Addr3 В-10 кВ Т-1 | [8 empty] | 3 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20304 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr3k | Akon 314 | 02 | CP1 Addr3 В-10 кВ Т-1 | [8 empty] | 3 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20302 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr3k | Akon 314 | 01 | CP1 Addr3 В-10 кВ Т-1 | [8 empty] | 3 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20301 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozirna | CP1 Addr3k | Akon 314 | ТК01 | CP1 Addr3 В-10 кВ Т-1 | [8 empty] | 3 | 5 | 0 | 0 | 1 | [18 empty] | N | 1 | 10301 |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP1 Addr5k | Akon 310 | ТВ01 | CP1 Addr5 В-10 кВ "Б. Гребля" | [8 empty] | 5 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 40503 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr5k | Akon 310 | 04 | CP1 Addr5 В-10 кВ "Б. Гребля" | [8 empty] | 5 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20505 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr5k | Akon 310 | 03 | CP1 Addr5 В-10 кВ "Б. Гребля" | [8 empty] | 5 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20504 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr5k | Akon 310 | 02 | CP1 Addr5 В-10 кВ "Б. Гребля" | [8 empty] | 5 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20502 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr5k | Akon 310 | 01 | CP1 Addr5 В-10 кВ "Б. Гребля" | [8 empty] | 5 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20501 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozirna | CP1 Addr5k | Akon 310 | ТК01 | CP1 Addr5 В-10 кВ "Б. Гребля" | [8 empty] | 5 | 5 | 0 | 0 | 1 | [18 empty] | N | 1 | 10501 |  |  | Y
MFI | [13 empty] | Y | added | Ozirna | CP1 Addr6k | Akon 310 | ТВ01 | CP1 Addr6 В-10 кВ "Сорокотяги" | [8 empty] | 6 | 3 | 16384 |  | 2 |  | Y | Integrated | 0.5 | [9 empty] | 32 bit floating point value (high word in first register) | -32768 | 32767 | 0 | 65535 |  | 1 | 40603 |  | Y | Y | Y | Off |  |  |  |  | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr6k | Akon 310 | 04 | CP1 Addr6 В-10 кВ "Сорокотяги" | [8 empty] | 6 | 2 | 3 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20605 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr6k | Akon 310 | 03 | CP1 Addr6 В-10 кВ "Сорокотяги" | [8 empty] | 6 | 2 | 2 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20604 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr6k | Akon 310 | 02 | CP1 Addr6 В-10 кВ "Сорокотяги" | [8 empty] | 6 | 2 | 1 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20602 | 2 | Y | Y | [6 empty] | N |  |  | Y
SPI | [5 empty] | N | N | [6 empty] | Y | added | Ozirna | CP1 Addr6k | Akon 310 | 01 | CP1 Addr6 В-10 кВ "Сорокотяги" | [8 empty] | 6 | 2 | 0 |  | 1 | 0 |  |  |  |  | N | 0 | 200 | 1 | 0 | [9 empty] | 1 | 20601 | 2 | Y | Y | [6 empty] | N |  |  | Y
SCO | [13 empty] | Y | added | Ozirna | CP1 Addr6k | Akon 310 | ТК01 | CP1 Addr6 В-10 кВ "Сорокотяги" | [8 empty] | 6 | 5 | 0 | 0 | 1 | [18 empty] | N | 1 | 10601 |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP1 Addr1 10 кВ "Резерв" | [32 empty] | 1 | 50101 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP1 Addr2 В-10 кВ "Межовий" | [32 empty] | 1 | 50201 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP1 Addr3 В-10 кВ Т-1 | [32 empty] | 1 | 50301 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP1 Addr5 В-10 кВ "Б. Гребля" | [32 empty] | 1 | 50501 |  | Y | Y | [6 empty] | N |  |  | Y
SEV | #048: Device/ RTU inoperable | [12 empty] | Y | added |  |  |  |  | CP1 Addr6 В-10 кВ "Сорокотяги" | [32 empty] | 1 | 50601 |  | Y | Y | [6 empty] | N |  |  | Y
_End

## Local IO
_EndColumn
Signal type | System data type | Type variant (AMI and EPI) | Process information (DCO and SCO) | 1 of n control group (ASO, BSO, DCO, DSO, FSO, RCO, SCO, TDC) | Control authority group (ASO, BSO, DCO, DSO, FSO, RCO, SCO, TDC) | Alarm for intermediate position (DPI) | Alarm for OFF position (DPI, SPI) | Alarm for ON position (DPI, SPI) | Alarm for indeterminate position (DPI) | Monitoring data blocking group (Input only) | Scaled values (AMI/DMI/ASO/DSO) | Maximum value (100%) (AMI/DMI/ASO/DSO) | Minimum value (-100%) (AMI/DMI/ASO/DSO) | Engineering unit (AMI/DMI/ASO/DSO/FSO/MFI) | RTUtil500 import | Export status | STA | BAY | DEV | SCADA object | File Type (FTR and FDR) | Directory | Num. of archived files in dir. | Time of storage in directory | Dir. search pattern | Directory path | Time interval | Max. info elements | PLC Function name | PLC task name | Logic Function name | ASDU address | Information object | Priority (SPI, DPI, DMI, EPI, STI) | Transmit with timestamp | In use | Spontaneous transmission (AMI, ITI, MFI) | Background cycle (AMI, MFI) | Transmission format (AMI, ASO, DSO) | Maximum value (100%) (AMI, ASO, DSO) | Minimum value (-100%) (AMI) | Interrogation group number (AMI, BSI, DMI, DPI, EPI, MFI, SEV, SPI, STI) | Include in sequence of event file (AMI, BSI, DMI, DPI, EPI, ITI, MFI, SEV, SPI, STI) | Max. contained ASDUs (FTR type 'Seq. of events') | Sections per file (FTR type 'Seq. of events') | Store in buffer (AMI, BSI, DMI, DPI, ITI, MFI, SEV, SPI, STI) | Update event filter (DPI, SPI)
Signal | [16 empty] | Process Object Identification |  |  |  | FTR | [7 empty] | PLC Function |  | Logic Function | SCADA (IEC 60870-5-104)-Address |  | SCADA (IEC 60870-5-104)-Host Parameter
5 ASCII | 4 ASCII | ASCII | ASCII | 1 .. 200 | 1 .. 200 | Y / N | Y / N | Y / N | Y / N | 1 .. 200 | Y / N | -3.4E+38 .. 3.4E+38 | -3.4E+38 .. 3.4E+38 | 32 ASCII | Y / N | Added / Modified / Deleted | 12 ASCII | 12 ASCII | 45 ASCII | 59 ASCII | Value from list | ASCII | 1 .. 255 | 1 .. 365 | ASCII | ASCII | 1 .. 918000 | 1 .. 3600 | ASCII | ASCII | ASCII | 0 .. 65535 | 0 .. 16777215 | 1 / 2 | Y / N | Y / N | Y / N | Off, 1, 2, 4, 5, 8, 10, 16, 30, 60 sec, 2, 5, 10 min | Normalized, Scaled | -32768 .. 32767 | -32768 .. 32767 | 1 .. 16 | Y / N | 1 ... 5000 | 1 ... 100 | Y / N | 1 .. 300
STTY | STDT | STTV | STPI | COGR | COAU | ALINT | ALOFF | ALON | ALIND | MBGR | SCVEN | SCVMA | SCVMI | SCVEU | STIM | STATUS | OI01 | OI02 | OI03 | OI04 | FTTY | FDR | FDDS | FDAD | FDSP | FDDP | FDTI | FDMX | RUFN | RUTN | LFN | E101 | E102 | E1PR | E1TI | E1IU | E1SP | E1BG | E1TF | E1MV | E1MNV | E1IGN | E1SEF | E1SOEMC | E1SOESP | E1PUB | E1UEF
SEV | #023: RTU is faulty | [13 empty] | Y | added | [15 empty] | 1 | 50017 |  | Y | Y | [6 empty] | N |  |  | Y
_End

## IEC61850 Defines (hidden)
#VERSION | 9 | 5 | 1 | 0
LN Group List | LN Group | LN Class List | LN Prefix | GGIO Prefix | LN Class | Data Object List | Data Object Type | Data Object | Data Attribute List | DataObjectNameList | CommonDataClassList | CDCDataAttributeList | DataTypeList | DataAttributeList | FunctionCodeList
System_LN | System_LN | LLN0 | LN_Prefix | SP | LLN0 | Loc | SPS | Loc | stVal | A.neut | CMV | ACD_dirGeneral | Enum | actVal | ST
LN_Control | LN_Control | CSWI |  | SP8 | [5 empty] | A.phsA | CMV | ACD_dirNeut | Enum | cVal.mag.f | MX
LN_Generic_IO |  | CILO |  | SP16 | CSWI | Loc | SPS | Pos | Oper.ctlVal | A.phsB | CMV | ACD_dirPhsA | Enum | dirGeneral | ST
LN_Metering |  | CALH |  | DP |  | Pos | DPC |  | stVal | A.phsC | CMV | ACD_dirPhsB | Enum | dirNeut | ST
LN_Protection | LN_Generic_IO | GAPC |  | DP8 | [5 empty] | Amp | MV | ACD_dirPhsC | Enum | dirPhsA | ST
LN_Protection_Related |  | GGIO |  | INS | CILO | EnaOpn | SPS | EnaOpn | stVal | AnIn | MV | ACD_general | BOOLEAN | dirPhsB | ST
LN_Sensors | LN_Metering | MMTR |  | BCR |  | EnaCls | SPS |  |  | AnIn1 | MV | ACD_neut | BOOLEAN | dirPhsC | ST
LN_Switchgear |  | MMXN |  | MV |  |  |  | EnaCls | stVal | AnIn2 | MV | ACD_phsA | BOOLEAN | frVal | ST
LN_Power_Transformer |  | MMXU |  | MV8 | CALH | GrAlm | SPS |  |  | AnIn3 | MV | ACD_phsB | BOOLEAN | general | ST
LN_Power_Equipment | LN_Protection | PTOC |  | CMV |  |  |  | GrAlm | stVal | AnIn4 | MV | ACD_phsC | BOOLEAN | mag.f | MX
|  | PDIS |  | SC | GAPC | Str | ACD |  |  | AnIn5 | MV | ACT_general | BOOLEAN | neut | ST
|  | PDIF |  | SC8 |  | Op | ACT | Ind | stVal | AnIn6 | MV | ACT_neut | BOOLEAN | Oper.ctlVal | CO
|  | PTOF |  | SC16 | [5 empty] | AnIn7 | MV | ACT_phsA | BOOLEAN | phsA | ST
|  | PTUF |  | DC | SPGGIO | Ind | SPS | Ind1 | stVal | AnIn8 | MV | ACT_phsB | BOOLEAN | phsB | ST
|  | PTOV |  | DC8 | [5 empty] | AutoRecSt | INS | ACT_phsC | BOOLEAN | phsC | ST
|  | PTUV |  | INC | SP8GGIO | Ind1 | SPS | Ind2 | stVal | BlkCls | SPC | BCR_actVal | INT32 | stVal | ST
|  | PSDE |  | BSC |  | Ind2 | SPS |  |  | BlkOpn | SPC | BCR_frVal | INT32 | valWTr.posVal | ST
|  | PTEF |  |  |  | Ind3 | SPS | Ind3 | stVal | CBOpCap | INS | BSC_Oper.ctlVal | CodedEnum2
|  | PSCH |  |  |  | Ind4 | SPS |  |  | ColTapPos | ISC | BSC_valWTr.posVal | INT8
|  | PTRC |  |  |  | Ind5 | SPS | Ind4 | stVal | CVIn | CMV | CMV_cVal.mag.f | FLOAT32
| LN_Protection_Related | RBRF |  |  |  | Ind6 | SPS |  |  | DenAlm | SPS | DPC_Oper.ctlVal | BOOLEAN
|  | RREC |  |  |  | Ind7 | SPS | Ind5 | stVal | DPCSO | DPC | DPC_stVal | Dbpos
|  | RSYN |  |  |  | Ind8 | SPS |  |  | DPCSO1 | DPC | DPS_stVal | Dbpos
| LN_Sensors | SIMG | [5 empty] | Ind6 | stVal | DPCSO2 | DPC | INC_Oper.ctlVal | INT32
|  | SIML |  |  | SP16GGIO | Ind1 | SPS |  |  | DPCSO3 | DPC | INC_stVal | INT32
| LN_Switchgear | XCBR |  |  |  | Ind2 | SPS | Ind7 | stVal | DPCSO4 | DPC | INS_stVal | INT32
|  | XSWI |  |  |  | Ind3 | SPS |  |  | DPCSO5 | DPC | ISC_Oper.ctlVal | INT8
| LN_Power_Transformer | YLTC |  |  |  | Ind4 | SPS | Ind8 | stVal | DPCSO6 | DPC | ISC_valWTr.posVal | INT8
|  | YEFN |  |  |  | Ind5 | SPS |  |  | DPCSO7 | DPC | MV_mag.f | FLOAT32
| LN_Power_Equipment | ZAXN |  |  |  | Ind6 | SPS | Ind9 | stVal | DPCSO8 | DPC | SPC_Oper.ctlVal | BOOLEAN
[6 empty] | Ind7 | SPS |  |  | DPI | DPS | SPC_stVal | BOOLEAN
[6 empty] | Ind8 | SPS | Ind10 | stVal | DPI1 | DPS | SPS_stVal | BOOLEAN
[6 empty] | Ind9 | SPS |  |  | DPI2 | DPS
[6 empty] | Ind10 | SPS | Ind11 | stVal | DPI3 | DPS
[6 empty] | Ind11 | SPS |  |  | DPI4 | DPS
[6 empty] | Ind12 | SPS | Ind12 | stVal | DPI5 | DPS
[6 empty] | Ind13 | SPS |  |  | DPI6 | DPS
[6 empty] | Ind14 | SPS | Ind13 | stVal | DPI7 | DPS
[6 empty] | Ind15 | SPS |  |  | DPI8 | DPS
[6 empty] | Ind16 | SPS | Ind14 | stVal | ECA | MV
[10 empty] | EEHealth | INS
[5 empty] | DPGGIO | DPI | DPS | Ind15 | stVal | EnaCls | SPS
[10 empty] | EnaOpn | SPS
[5 empty] | DP8GGIO | DPI1 | DPS | Ind16 | stVal | EndPosL | SPS
[6 empty] | DPI2 | DPS |  |  | EndPosR | SPS
[6 empty] | DPI3 | DPS | DPI | stVal | EPI | ACT
[6 empty] | DPI4 | DPS |  |  | GrAlm | SPS
[6 empty] | DPI5 | DPS | DPI1 | stVal | Hz | MV
[6 empty] | DPI6 | DPS |  |  | Imp | CMV
[6 empty] | DPI7 | DPS | DPI2 | stVal | Ind | SPS
[6 empty] | DPI8 | DPS |  |  | Ind1 | SPS
[8 empty] | DPI3 | stVal | Ind10 | SPS
[5 empty] | INSGGIO | IntIn | INS |  |  | Ind11 | SPS
[8 empty] | DPI4 | stVal | Ind12 | SPS
[5 empty] | ACTGGIO | EPI | ACT |  |  | Ind13 | SPS
[8 empty] | DPI5 | stVal | Ind14 | SPS
[5 empty] | BCRGGIO | ITI | BCR |  |  | Ind15 | SPS
[8 empty] | DPI6 | stVal | Ind16 | SPS
[5 empty] | MVGGIO | AnIn | MV |  |  | Ind2 | SPS
[8 empty] | DPI7 | stVal | Ind3 | SPS
[5 empty] | MV8GGIO | AnIn1 | MV |  |  | Ind4 | SPS
[6 empty] | AnIn2 | MV | DPI8 | stVal | Ind5 | SPS
[6 empty] | AnIn3 | MV |  |  | Ind6 | SPS
[6 empty] | AnIn4 | MV | IntIn | stVal | Ind7 | SPS
[6 empty] | AnIn5 | MV |  |  | Ind8 | SPS
[6 empty] | AnIn6 | MV | EPI | general | Ind9 | SPS
[6 empty] | AnIn7 | MV |  | phsA | InsAlm | SPS
[6 empty] | AnIn8 | MV |  | phsB | IntIn | INS
[9 empty] | phsC | ISCSO | INC
[5 empty] | CMVGGIO | CVIn | CMV |  | neut | ITI | BCR
[10 empty] | Loc | SPS
[5 empty] | SCGGIO | SPCSO | SPC | ITI | actVal | Op | ACT
[9 empty] | frVal | OpCnt | INS
[5 empty] | SC8GGIO | SPCSO1 | SPC |  |  | OpEx | ACT
[6 empty] | SPCSO2 | SPC | AnIn | mag.f | OpIn | ACT
[6 empty] | SPCSO3 | SPC |  |  | PF.neut | CMV
[6 empty] | SPCSO4 | SPC | AnIn1 | mag.f | PF.phsA | CMV
[6 empty] | SPCSO5 | SPC |  |  | PF.phsB | CMV
[6 empty] | SPCSO6 | SPC | AnIn2 | mag.f | PF.phsC | CMV
[6 empty] | SPCSO7 | SPC |  |  | PhV.neut | CMV
[6 empty] | SPCSO8 | SPC | AnIn3 | mag.f | PhV.phsA | CMV
[10 empty] | PhV.phsB | CMV
[5 empty] | SC16GGIO | SPCSO1 | SPC | AnIn4 | mag.f | PhV.phsC | CMV
[6 empty] | SPCSO2 | SPC |  |  | PhyHealth | INS
[6 empty] | SPCSO3 | SPC | AnIn5 | mag.f | Pos | DPC
[6 empty] | SPCSO4 | SPC |  |  | PPV.phsAB | CMV
[6 empty] | SPCSO5 | SPC | AnIn6 | mag.f | PPV.phsBC | CMV
[6 empty] | SPCSO6 | SPC |  |  | PPV.phsCA | CMV
[6 empty] | SPCSO7 | SPC | AnIn7 | mag.f | PresAlm | SPS
[6 empty] | SPCSO8 | SPC |  |  | PresTr | SPS
[6 empty] | SPCSO9 | SPC | AnIn8 | mag.f | ProRx | SPS
[6 empty] | SPCSO10 | SPC |  |  | ProTx | SPS
[6 empty] | SPCSO11 | SPC | CVIn | cVal.mag.f | PwrFact | MV
[6 empty] | SPCSO12 | SPC |  |  | RCO | BSC
[6 empty] | SPCSO13 | SPC | SPCSO | Oper.ctlVal | Rel | SPS
[6 empty] | SPCSO14 | SPC |  | stVal | SPCSO | SPC
[6 empty] | SPCSO15 | SPC |  |  | SPCSO1 | SPC
[6 empty] | SPCSO16 | SPC | SPCSO1 | Oper.ctlVal | SPCSO10 | SPC
[9 empty] | stVal | SPCSO11 | SPC
[5 empty] | DCGGIO | DPCSO | DPC |  |  | SPCSO12 | SPC
[8 empty] | SPCSO2 | Oper.ctlVal | SPCSO13 | SPC
[5 empty] | DC8GGIO | DPCSO1 | DPC |  | stVal | SPCSO14 | SPC
[6 empty] | DPCSO2 | DPC |  |  | SPCSO15 | SPC
[6 empty] | DPCSO3 | DPC | SPCSO3 | Oper.ctlVal | SPCSO16 | SPC
[6 empty] | DPCSO4 | DPC |  | stVal | SPCSO2 | SPC
[6 empty] | DPCSO5 | DPC |  |  | SPCSO3 | SPC
[6 empty] | DPCSO6 | DPC | SPCSO4 | Oper.ctlVal | SPCSO4 | SPC
[6 empty] | DPCSO7 | DPC |  | stVal | SPCSO5 | SPC
[6 empty] | DPCSO8 | DPC |  |  | SPCSO6 | SPC
[8 empty] | SPCSO5 | Oper.ctlVal | SPCSO7 | SPC
[5 empty] | INCGGIO | ISCSO | INC |  | stVal | SPCSO8 | SPC
[10 empty] | SPCSO9 | SPC
[5 empty] | BSCGGIO | RCO | BSC | SPCSO6 | Oper.ctlVal | Str | ACD
[9 empty] | stVal | SwOpCap | INS
[5 empty] | MMTR | TotVAh | BCR |  |  | SwTyp | INS
[6 empty] | TotWh | BCR | SPCSO7 | Oper.ctlVal | TapChg | BSC
[6 empty] | TotVArh | BCR |  | stVal | TmpAlm | SPS
[10 empty] | TotPF | MV
[5 empty] | MMXN | Amp | MV | SPCSO8 | Oper.ctlVal | TotVA | MV
[6 empty] | Vol | MV |  | stVal | TotVAh | BCR
[6 empty] | Watt | MV |  |  | TotVAr | MV
[6 empty] | VolAmpr | MV | SPCSO9 | Oper.ctlVal | TotVArh | BCR
[6 empty] | VolAmp | MV |  | stVal | TotW | MV
[6 empty] | PwrFact | MV |  |  | TotWh | BCR
[6 empty] | Imp | CMV | SPCSO10 | Oper.ctlVal | VA.neut | CMV
[6 empty] | Hz | MV |  | stVal | VA.phsA | CMV
[10 empty] | VA.phsB | CMV
[5 empty] | MMXU | TotW | MV | SPCSO11 | Oper.ctlVal | VA.phsC | CMV
[6 empty] | TotVAr | MV |  | stVal | VAr.neut | CMV
[6 empty] | TotVA | MV |  |  | VAr.phsA | CMV
[6 empty] | TotPF | MV | SPCSO12 | Oper.ctlVal | VAr.phsB | CMV
[6 empty] | Hz | MV |  | stVal | VAr.phsC | CMV
[6 empty] | PPV.phsAB | CMV |  |  | Vol | MV
[6 empty] | PPV.phsBC | CMV | SPCSO13 | Oper.ctlVal | VolAmp | MV
[6 empty] | PPV.phsCA | CMV |  | stVal | VolAmpr | MV
[6 empty] | PhV.phsA | CMV |  |  | W.neut | CMV
[6 empty] | PhV.phsB | CMV | SPCSO14 | Oper.ctlVal | W.phsA | CMV
[6 empty] | PhV.phsC | CMV |  | stVal | W.phsB | CMV
[6 empty] | PhV.neut | CMV |  |  | W.phsC | CMV
[6 empty] | A.phsA | CMV | SPCSO15 | Oper.ctlVal | Watt | MV
[6 empty] | A.phsB | CMV |  | stVal | Z.neut | CMV
[6 empty] | A.phsC | CMV |  |  | Z.phsA | CMV
[6 empty] | A.neut | CMV | SPCSO16 | Oper.ctlVal | Z.phsB | CMV
[6 empty] | W.phsA | CMV |  | stVal | Z.phsC | CMV
[6 empty] | W.phsB | CMV
[6 empty] | W.phsC | CMV | DPCSO | Oper.ctlVal
[6 empty] | W.neut | CMV |  | stVal
[6 empty] | VAr.phsA | CMV
[6 empty] | VAr.phsB | CMV | DPCSO1 | Oper.ctlVal
[6 empty] | VAr.phsC | CMV |  | stVal
[6 empty] | VAr.neut | CMV
[6 empty] | VA.phsA | CMV | DPCSO2 | Oper.ctlVal
[6 empty] | VA.phsB | CMV |  | stVal
[6 empty] | VA.phsC | CMV
[6 empty] | VA.neut | CMV | DPCSO3 | Oper.ctlVal
[6 empty] | PF.phsA | CMV |  | stVal
[6 empty] | PF.phsB | CMV
[6 empty] | PF.phsC | CMV | DPCSO4 | Oper.ctlVal
[6 empty] | PF.neut | CMV |  | stVal
[6 empty] | Z.phsA | CMV
[6 empty] | Z.phsB | CMV | DPCSO5 | Oper.ctlVal
[6 empty] | Z.phsC | CMV |  | stVal
[6 empty] | Z.neut | CMV
[8 empty] | DPCSO6 | Oper.ctlVal
[5 empty] | PTOC | Str | ACD |  | stVal
[6 empty] | Op | ACT
[8 empty] | DPCSO7 | Oper.ctlVal
[5 empty] | PDIS | Str | ACD |  | stVal
[6 empty] | Op | ACT
[8 empty] | DPCSO8 | Oper.ctlVal
[5 empty] | PDIF | Op | ACT |  | stVal
[5 empty] | PTOF | Str | ACD | ISCSO | Oper.ctlVal
[6 empty] | Op | ACT |  | stVal
[5 empty] | PTUF | Str | ACD | RCO | Oper.ctlVal
[6 empty] | Op | ACT |  | valWTr.posVal
[5 empty] | PTOV | Str | ACD | TotVAh | actVal
[6 empty] | Op | ACT |  | frVal
[5 empty] | PTUV | Str | ACD | TotWh | actVal
[6 empty] | Op | ACT |  | frVal
[5 empty] | PSDE | Str | ACD | TotVArh | actVal
[6 empty] | Op | ACT |  | frVal
[5 empty] | PTEF | Str | ACD | Amp | mag.f
[6 empty] | Op | ACT
[8 empty] | Vol | mag.f
[5 empty] | PSCH | ProTx | SPS
[6 empty] | ProRx | SPS | Watt | mag.f
[6 empty] | Str | ACD
[6 empty] | Op | ACT | VolAmpr | mag.f
[5 empty] | PTRC | Str | ACD | VolAmp | mag.f
[6 empty] | Op | ACT
[8 empty] | PwrFact | mag.f
[5 empty] | RBRF | OpEx | ACT
[6 empty] | OpIn | ACT | Imp | cVal.mag.f
[5 empty] | RREC | Op | ACT | Hz | mag.f
[6 empty] | AutoRecSt | INS
[8 empty] | TotW | mag.f
[5 empty] | RSYN | Rel | SPS
[8 empty] | TotVAr | mag.f
[5 empty] | SIMG | InsAlm | SPS
[6 empty] | PresAlm | SPS | TotVA | mag.f
[6 empty] | DenAlm | SPS
[6 empty] | TmpAlm | SPS | TotPF | mag.f
[5 empty] | SIML | InsAlm | SPS | PPV.phsAB | cVal.mag.f
[6 empty] | TmpAlm | SPS
[6 empty] | PresTr | SPS | PPV.phsBC | cVal.mag.f
[6 empty] | PresAlm | SPS
[8 empty] | PPV.phsCA | cVal.mag.f
[5 empty] | XCBR | Loc | SPS
[6 empty] | EEHealth | INS | PhV.phsA | cVal.mag.f
[6 empty] | OpCnt | INS
[6 empty] | Pos | DPC | PhV.phsB | cVal.mag.f
[6 empty] | BlkOpn | SPC
[6 empty] | BlkCls | SPC | PhV.phsC | cVal.mag.f
[6 empty] | CBOpCap | INS
[8 empty] | PhV.neut | cVal.mag.f
[5 empty] | XSWI | Loc | SPS
[6 empty] | EEHealth | INS | A.phsA | cVal.mag.f
[6 empty] | OpCnt | INS
[6 empty] | Pos | DPC | A.phsB | cVal.mag.f
[6 empty] | BlkOpn | SPC
[6 empty] | BlkCls | SPC | A.phsC | cVal.mag.f
[6 empty] | SwTyp | INS
[6 empty] | SwOpCap | INS | A.neut | cVal.mag.f
[5 empty] | YLTC | EEHealth | INS | W.phsA | cVal.mag.f
[6 empty] | TapChg | BSC
[6 empty] | EndPosR | SPS | W.phsB | cVal.mag.f
[6 empty] | EndPosL | SPS
[8 empty] | W.phsC | cVal.mag.f
[5 empty] | YEFN | EEHealth | INS
[6 empty] | Loc | SPS | W.neut | cVal.mag.f
[6 empty] | ECA | MV
[6 empty] | ColTapPos | ISC | VAr.phsA | cVal.mag.f
[5 empty] | ZAXN | EEHealth | INS | VAr.phsB | cVal.mag.f
[8 empty] | VAr.phsC | cVal.mag.f
[8 empty] | VAr.neut | cVal.mag.f
[8 empty] | VA.phsA | cVal.mag.f
[8 empty] | VA.phsB | cVal.mag.f
[8 empty] | VA.phsC | cVal.mag.f
[8 empty] | VA.neut | cVal.mag.f
[8 empty] | PF.phsA | cVal.mag.f
[8 empty] | PF.phsB | cVal.mag.f
[8 empty] | PF.phsC | cVal.mag.f
[8 empty] | PF.neut | cVal.mag.f
[8 empty] | Z.phsA | cVal.mag.f
[8 empty] | Z.phsB | cVal.mag.f
[8 empty] | Z.phsC | cVal.mag.f
[8 empty] | Z.neut | cVal.mag.f
[8 empty] | Str | general
dirGeneral
phsA
dirPhsA
phsB
dirPhsB
phsC
dirPhsC
neut
dirNeut
[8 empty] | Op | general
phsA
phsB
phsC
neut
[8 empty] | ProTx | stVal
[8 empty] | ProRx | stVal
[8 empty] | OpEx | general
phsA
phsB
phsC
neut
[8 empty] | OpIn | general
phsA
phsB
phsC
neut
[8 empty] | AutoRecSt | stVal
[8 empty] | Rel | stVal
[8 empty] | InsAlm | stVal
[8 empty] | PresAlm | stVal
[8 empty] | DenAlm | stVal
[8 empty] | TmpAlm | stVal
[8 empty] | PresTr | stVal
[8 empty] | OpCnt | stVal
[8 empty] | BlkOpn | Oper.ctlVal
stVal
[8 empty] | BlkCls | Oper.ctlVal
stVal
[8 empty] | CBOpCap | stVal
[8 empty] | SwTyp | stVal
[8 empty] | SwOpCap | stVal
[8 empty] | EEHealth | stVal
[8 empty] | TapChg | Oper.ctlVal
valWTr.posVal
[8 empty] | EndPosR | stVal
[8 empty] | EndPosL | stVal
[8 empty] | ECA | mag.f
[8 empty] | ColTapPos | Oper.ctlVal
valWTr.posVal

## IEC61850 Edition2 Defines (hidden)
#EDITION 2
LN Group List | LN Group | LN Class List | LN Prefix | GGIO Prefix | LN Class | Data Object List | Data Object Type | Data Object | Data Attribute List | DataObjectNameList | CommonDataClassList | CDCDataAttributeList | DataTypeList | DataAttributeList | FunctionCodeList
System_LN | System_LN | LLN0 | LN_Prefix | SP | LLN0 | Loc | SPS | Loc | stVal | A.neut | CMV | ACD_dirGeneral | Enum | actVal | ST
LN_Control | LN_Control | CSWI |  | SP8 | [5 empty] | A.phsA | CMV | ACD_dirNeut | Enum | cVal.mag.f | MX
LN_Generic_IO |  | CILO |  | SP16 | CSWI | Loc | SPS | Pos | Oper.ctlVal | A.phsB | CMV | ACD_dirPhsA | Enum | dirGeneral | ST
LN_Metering |  | CALH |  | DP |  | Pos | DPC |  | stVal | A.phsC | CMV | ACD_dirPhsB | Enum | dirNeut | ST
LN_Protection | LN_Generic_IO | GAPC |  | DP8 | [5 empty] | Amp | MV | ACD_dirPhsC | Enum | dirPhsA | ST
LN_Protection_Related |  | GGIO |  | INS | CILO | EnaOpn | SPS | EnaOpn | stVal | AnIn1 | MV | ACD_general | BOOLEAN | dirPhsB | ST
LN_Sensors | LN_Metering | MMTR |  | BCR |  | EnaCls | SPS |  |  | AnIn2 | MV | ACD_neut | BOOLEAN | dirPhsC | ST
LN_Switchgear |  | MMXN |  | MV |  |  |  | EnaCls | stVal | AnIn3 | MV | ACD_phsA | BOOLEAN | frVal | ST
LN_Power_Transformer |  | MMXU |  | MV8 | CALH | GrAlm | SPS |  |  | AnIn4 | MV | ACD_phsB | BOOLEAN | general | ST
LN_Power_Equipment | LN_Protection | PTOC |  | CMV |  |  |  | GrAlm | stVal | AnIn5 | MV | ACD_phsC | BOOLEAN | mag.f | MX
|  | PDIS |  | SC | GAPC | Str | ACD |  |  | AnIn6 | MV | ACT_general | BOOLEAN | neut | ST
|  | PDIF |  | SC8 |  | Op | ACT | Ind1 | stVal | AnIn7 | MV | ACT_neut | BOOLEAN | Oper.ctlVal | CO
|  | PTOF |  | SC16 | [5 empty] | AnIn8 | MV | ACT_phsA | BOOLEAN | phsA | ST
|  | PTUF |  | DC | SPGGIO | Ind1 | SPS | Ind2 | stVal | AutoRecSt | ENS | ACT_phsB | BOOLEAN | phsB | ST
|  | PTOV |  | DC8 | [5 empty] | BlkCls | SPC | ACT_phsC | BOOLEAN | phsC | ST
|  | PTUV |  | INC | SP8GGIO | Ind1 | SPS | Ind3 | stVal | BlkOpn | SPC | BCR_actVal | INT64 | stVal | ST
|  | PSDE |  | BSC |  | Ind2 | SPS |  |  | CBOpCap | ENS | BCR_frVal | INT64 | valWTr.posVal | ST
|  | PTEF |  | ENS |  | Ind3 | SPS | Ind4 | stVal | ColPosA | MV | BSC_Oper.ctlVal | CodedEnum2
|  | PSCH |  |  |  | Ind4 | SPS |  |  | ColTapPos | ISC | BSC_valWTr.posVal | INT8
|  | PTRC |  |  |  | Ind5 | SPS | Ind5 | stVal | CVIn1 | CMV | CMV_cVal.mag.f | FLOAT32
| LN_Protection_Related | RBRF |  |  |  | Ind6 | SPS |  |  | DenAlm | SPS | DPC_Oper.ctlVal | BOOLEAN
|  | RREC |  |  |  | Ind7 | SPS | Ind6 | stVal | DPCSO1 | DPC | DPC_stVal | Dbpos
|  | RSYN |  |  |  | Ind8 | SPS |  |  | DPCSO2 | DPC | DPS_stVal | Dbpos
| LN_Sensors | SIMG | [5 empty] | Ind7 | stVal | DPCSO3 | DPC | ENS_stVal | Enum
|  | SIML |  |  | SP16GGIO | Ind1 | SPS |  |  | DPCSO4 | DPC | INC_Oper.ctlVal | INT32
| LN_Switchgear | XCBR |  |  |  | Ind2 | SPS | Ind8 | stVal | DPCSO5 | DPC | INC_stVal | INT32
|  | XSWI |  |  |  | Ind3 | SPS |  |  | DPCSO6 | DPC | INS_stVal | INT32
| LN_Power_Transformer | YLTC |  |  |  | Ind4 | SPS | Ind9 | stVal | DPCSO7 | DPC | ISC_Oper.ctlVal | INT8
|  | YEFN |  |  |  | Ind5 | SPS |  |  | DPCSO8 | DPC | ISC_valWTr.posVal | INT8
| LN_Power_Equipment | ZAXN |  |  |  | Ind6 | SPS | Ind10 | stVal | DPI1 | DPS | MV_mag.f | FLOAT32
[6 empty] | Ind7 | SPS |  |  | DPI2 | DPS | SPC_Oper.ctlVal | BOOLEAN
[6 empty] | Ind8 | SPS | Ind11 | stVal | DPI3 | DPS | SPC_stVal | BOOLEAN
[6 empty] | Ind9 | SPS |  |  | DPI4 | DPS | SPS_stVal | BOOLEAN
[6 empty] | Ind10 | SPS | Ind12 | stVal | DPI5 | DPS
[6 empty] | Ind11 | SPS |  |  | DPI6 | DPS
[6 empty] | Ind12 | SPS | Ind13 | stVal | DPI7 | DPS
[6 empty] | Ind13 | SPS |  |  | DPI8 | DPS
[6 empty] | Ind14 | SPS | Ind14 | stVal | EEHealth | ENS
[6 empty] | Ind15 | SPS |  |  | EnaCls | SPS
[6 empty] | Ind16 | SPS | Ind15 | stVal | EnaOpn | SPS
[10 empty] | EndPosL | SPS
[5 empty] | DPGGIO | DPI1 | DPS | Ind16 | stVal | EndPosR | SPS
[10 empty] | EPI1 | ACT
[5 empty] | DP8GGIO | DPI1 | DPS | DPI1 | stVal | GasInsAlm | SPS
[6 empty] | DPI2 | DPS |  |  | GasInsTr | SPS
[6 empty] | DPI3 | DPS | DPI2 | stVal | GrAlm | SPS
[6 empty] | DPI4 | DPS |  |  | Hz | MV
[6 empty] | DPI5 | DPS | DPI3 | stVal | Imp | CMV
[6 empty] | DPI6 | DPS |  |  | Ind1 | SPS
[6 empty] | DPI7 | DPS | DPI4 | stVal | Ind10 | SPS
[6 empty] | DPI8 | DPS |  |  | Ind11 | SPS
[8 empty] | DPI5 | stVal | Ind12 | SPS
[5 empty] | INSGGIO | IntIn1 | INS |  |  | Ind13 | SPS
[8 empty] | DPI6 | stVal | Ind14 | SPS
[5 empty] | ACTGGIO | EPI1 | ACT |  |  | Ind15 | SPS
[8 empty] | DPI7 | stVal | Ind16 | SPS
[5 empty] | BCRGGIO | ITI1 | BCR |  |  | Ind2 | SPS
[8 empty] | DPI8 | stVal | Ind3 | SPS
[5 empty] | MVGGIO | AnIn1 | MV |  |  | Ind4 | SPS
[8 empty] | IntIn1 | stVal | Ind5 | SPS
[5 empty] | MV8GGIO | AnIn1 | MV |  |  | Ind6 | SPS
[6 empty] | AnIn2 | MV | EPI1 | general | Ind7 | SPS
[6 empty] | AnIn3 | MV |  | phsA | Ind8 | SPS
[6 empty] | AnIn4 | MV |  | phsB | Ind9 | SPS
[6 empty] | AnIn5 | MV |  | phsC | InsAlm | SPS
[6 empty] | AnIn6 | MV |  | neut | IntIn1 | INS
[6 empty] | AnIn7 | MV |  |  | ISCSO1 | INC
[6 empty] | AnIn8 | MV | ITI1 | actVal | ITI1 | BCR
[9 empty] | frVal | Loc | SPS
[5 empty] | CMVGGIO | CVIn1 | CMV |  |  | Op | ACT
[8 empty] | AnIn1 | mag.f | OpCls | ACT
[5 empty] | SCGGIO | SPCSO1 | SPC |  |  | OpCnt | INS
[8 empty] | AnIn2 | mag.f | OpEx | ACT
[5 empty] | SC8GGIO | SPCSO1 | SPC |  |  | OpIn | ACT
[6 empty] | SPCSO2 | SPC | AnIn3 | mag.f | PF.neut | CMV
[6 empty] | SPCSO3 | SPC |  |  | PF.phsA | CMV
[6 empty] | SPCSO4 | SPC | AnIn4 | mag.f | PF.phsB | CMV
[6 empty] | SPCSO5 | SPC |  |  | PF.phsC | CMV
[6 empty] | SPCSO6 | SPC | AnIn5 | mag.f | PhV.neut | CMV
[6 empty] | SPCSO7 | SPC |  |  | PhV.phsA | CMV
[6 empty] | SPCSO8 | SPC | AnIn6 | mag.f | PhV.phsB | CMV
[10 empty] | PhV.phsC | CMV
[5 empty] | SC16GGIO | SPCSO1 | SPC | AnIn7 | mag.f | PhyHealth | ENS
[6 empty] | SPCSO2 | SPC |  |  | Pos | DPC
[6 empty] | SPCSO3 | SPC | AnIn8 | mag.f | PPV.phsAB | CMV
[6 empty] | SPCSO4 | SPC |  |  | PPV.phsBC | CMV
[6 empty] | SPCSO5 | SPC | CVIn1 | cVal.mag.f | PPV.phsCA | CMV
[6 empty] | SPCSO6 | SPC |  |  | PresAlm | SPS
[6 empty] | SPCSO7 | SPC | SPCSO1 | Oper.ctlVal | PresTr | SPS
[6 empty] | SPCSO8 | SPC |  | stVal | PwrFact | MV
[6 empty] | SPCSO9 | SPC |  |  | RCO1 | BSC
[6 empty] | SPCSO10 | SPC | SPCSO2 | Oper.ctlVal | Rel | SPS
[6 empty] | SPCSO11 | SPC |  | stVal | SPCSO1 | SPC
[6 empty] | SPCSO12 | SPC |  |  | SPCSO10 | SPC
[6 empty] | SPCSO13 | SPC | SPCSO3 | Oper.ctlVal | SPCSO11 | SPC
[6 empty] | SPCSO14 | SPC |  | stVal | SPCSO12 | SPC
[6 empty] | SPCSO15 | SPC |  |  | SPCSO13 | SPC
[6 empty] | SPCSO16 | SPC | SPCSO4 | Oper.ctlVal | SPCSO14 | SPC
[9 empty] | stVal | SPCSO15 | SPC
[5 empty] | DCGGIO | DPCSO1 | DPC |  |  | SPCSO16 | SPC
[8 empty] | SPCSO5 | Oper.ctlVal | SPCSO2 | SPC
[5 empty] | DC8GGIO | DPCSO1 | DPC |  | stVal | SPCSO3 | SPC
[6 empty] | DPCSO2 | DPC |  |  | SPCSO4 | SPC
[6 empty] | DPCSO3 | DPC | SPCSO6 | Oper.ctlVal | SPCSO5 | SPC
[6 empty] | DPCSO4 | DPC |  | stVal | SPCSO6 | SPC
[6 empty] | DPCSO5 | DPC |  |  | SPCSO7 | SPC
[6 empty] | DPCSO6 | DPC | SPCSO7 | Oper.ctlVal | SPCSO8 | SPC
[6 empty] | DPCSO7 | DPC |  | stVal | SPCSO9 | SPC
[6 empty] | DPCSO8 | DPC |  |  | Str | ACD
[8 empty] | SPCSO8 | Oper.ctlVal | SwOpCap | ENS
[5 empty] | INCGGIO | ISCSO1 | INC |  | stVal | SwTyp | ENS
[10 empty] | TapChg | BSC
[5 empty] | BSCGGIO | RCO1 | BSC | SPCSO9 | Oper.ctlVal | TmpAlm | SPS
[9 empty] | stVal | TotPF | MV
[5 empty] | ENSGGIO | EEHealth | ENS |  |  | TotVA | MV
[8 empty] | SPCSO10 | Oper.ctlVal | TotVAh | BCR
[5 empty] | MMTR | TotVAh | BCR |  | stVal | TotVAr | MV
[6 empty] | TotWh | BCR |  |  | TotVArh | BCR
[6 empty] | TotVArh | BCR | SPCSO11 | Oper.ctlVal | TotW | MV
[9 empty] | stVal | TotWh | BCR
[5 empty] | MMXN | Amp | MV |  |  | VA.neut | CMV
[6 empty] | Vol | MV | SPCSO12 | Oper.ctlVal | VA.phsA | CMV
[6 empty] | Watt | MV |  | stVal | VA.phsB | CMV
[6 empty] | VolAmpr | MV |  |  | VA.phsC | CMV
[6 empty] | VolAmp | MV | SPCSO13 | Oper.ctlVal | VAr.neut | CMV
[6 empty] | PwrFact | MV |  | stVal | VAr.phsA | CMV
[6 empty] | Imp | CMV |  |  | VAr.phsB | CMV
[6 empty] | Hz | MV | SPCSO14 | Oper.ctlVal | VAr.phsC | CMV
[9 empty] | stVal | Vol | MV
[5 empty] | MMXU | TotW | MV |  |  | VolAmp | MV
[6 empty] | TotVAr | MV | SPCSO15 | Oper.ctlVal | VolAmpr | MV
[6 empty] | TotVA | MV |  | stVal | W.neut | CMV
[6 empty] | TotPF | MV |  |  | W.phsA | CMV
[6 empty] | Hz | MV | SPCSO16 | Oper.ctlVal | W.phsB | CMV
[6 empty] | PPV.phsAB | CMV |  | stVal | W.phsC | CMV
[6 empty] | PPV.phsBC | CMV |  |  | Watt | MV
[6 empty] | PPV.phsCA | CMV | DPCSO1 | Oper.ctlVal | Z.neut | CMV
[6 empty] | PhV.phsA | CMV |  | stVal | Z.phsA | CMV
[6 empty] | PhV.phsB | CMV |  |  | Z.phsB | CMV
[6 empty] | PhV.phsC | CMV | DPCSO2 | Oper.ctlVal | Z.phsC | CMV
[6 empty] | PhV.neut | CMV |  | stVal
[6 empty] | A.phsA | CMV
[6 empty] | A.phsB | CMV | DPCSO3 | Oper.ctlVal
[6 empty] | A.phsC | CMV |  | stVal
[6 empty] | A.neut | CMV
[6 empty] | W.phsA | CMV | DPCSO4 | Oper.ctlVal
[6 empty] | W.phsB | CMV |  | stVal
[6 empty] | W.phsC | CMV
[6 empty] | W.neut | CMV | DPCSO5 | Oper.ctlVal
[6 empty] | VAr.phsA | CMV |  | stVal
[6 empty] | VAr.phsB | CMV
[6 empty] | VAr.phsC | CMV | DPCSO6 | Oper.ctlVal
[6 empty] | VAr.neut | CMV |  | stVal
[6 empty] | VA.phsA | CMV
[6 empty] | VA.phsB | CMV | DPCSO7 | Oper.ctlVal
[6 empty] | VA.phsC | CMV |  | stVal
[6 empty] | VA.neut | CMV
[6 empty] | PF.phsA | CMV | DPCSO8 | Oper.ctlVal
[6 empty] | PF.phsB | CMV |  | stVal
[6 empty] | PF.phsC | CMV
[6 empty] | PF.neut | CMV | ISCSO1 | Oper.ctlVal
[6 empty] | Z.phsA | CMV |  | stVal
[6 empty] | Z.phsB | CMV
[6 empty] | Z.phsC | CMV | RCO1 | Oper.ctlVal
[6 empty] | Z.neut | CMV |  | valWTr.posVal
[5 empty] | PTOC | Str | ACD | TotVAh | actVal
[6 empty] | Op | ACT |  | frVal
[5 empty] | PDIS | Str | ACD | TotWh | actVal
[6 empty] | Op | ACT |  | frVal
[5 empty] | PDIF | Op | ACT | TotVArh | actVal
frVal
[5 empty] | PTOF | Str | ACD
[6 empty] | Op | ACT | Amp | mag.f
[5 empty] | PTUF | Str | ACD | Vol | mag.f
[6 empty] | Op | ACT
[8 empty] | Watt | mag.f
[5 empty] | PTOV | Str | ACD
[6 empty] | Op | ACT | VolAmpr | mag.f
[5 empty] | PTUV | Str | ACD | VolAmp | mag.f
[6 empty] | Op | ACT
[8 empty] | PwrFact | mag.f
[5 empty] | PSDE | Str | ACD
[6 empty] | Op | ACT | Imp | cVal.mag.f
[5 empty] | PTEF | Str | ACD | Hz | mag.f
[6 empty] | Op | ACT
[8 empty] | TotW | mag.f
[5 empty] | PSCH | Op | ACT
[8 empty] | TotVAr | mag.f
[5 empty] | PTRC | Str | ACD
[6 empty] | Op | ACT | TotVA | mag.f
[5 empty] | RBRF | OpEx | ACT | TotPF | mag.f
[6 empty] | OpIn | ACT
[8 empty] | PPV.phsAB | cVal.mag.f
[5 empty] | RREC | OpCls | ACT
[6 empty] | AutoRecSt | ENS | PPV.phsBC | cVal.mag.f
[5 empty] | RSYN | Rel | SPS | PPV.phsCA | cVal.mag.f
[5 empty] | SIMG | InsAlm | SPS | PhV.phsA | cVal.mag.f
[6 empty] | PresAlm | SPS
[6 empty] | DenAlm | SPS | PhV.phsB | cVal.mag.f
[6 empty] | TmpAlm | SPS
[8 empty] | PhV.phsC | cVal.mag.f
[5 empty] | SIML | InsAlm | SPS
[6 empty] | TmpAlm | SPS | PhV.neut | cVal.mag.f
[6 empty] | GasInsAlm | SPS
[6 empty] | GasInsTr | SPS | A.phsA | cVal.mag.f
[5 empty] | XCBR | Loc | SPS | A.phsB | cVal.mag.f
[6 empty] | EEHealth | ENS
[6 empty] | OpCnt | INS | A.phsC | cVal.mag.f
[6 empty] | Pos | DPC
[6 empty] | BlkOpn | SPC | A.neut | cVal.mag.f
[6 empty] | BlkCls | SPC
[6 empty] | CBOpCap | ENS | W.phsA | cVal.mag.f
[5 empty] | XSWI | Loc | SPS | W.phsB | cVal.mag.f
[6 empty] | EEHealth | ENS
[6 empty] | OpCnt | INS | W.phsC | cVal.mag.f
[6 empty] | Pos | DPC
[6 empty] | BlkOpn | SPC | W.neut | cVal.mag.f
[6 empty] | BlkCls | SPC
[6 empty] | SwTyp | ENS | VAr.phsA | cVal.mag.f
[6 empty] | SwOpCap | ENS
[8 empty] | VAr.phsB | cVal.mag.f
[5 empty] | YLTC | EEHealth | ENS
[6 empty] | TapChg | BSC | VAr.phsC | cVal.mag.f
[6 empty] | EndPosR | SPS
[6 empty] | EndPosL | SPS | VAr.neut | cVal.mag.f
[5 empty] | YEFN | EEHealth | ENS | VA.phsA | cVal.mag.f
[6 empty] | Loc | SPS
[6 empty] | ColPosA | MV | VA.phsB | cVal.mag.f
[6 empty] | ColTapPos | ISC
[8 empty] | VA.phsC | cVal.mag.f
[5 empty] | ZAXN | EEHealth | ENS
[8 empty] | VA.neut | cVal.mag.f
[8 empty] | PF.phsA | cVal.mag.f
[8 empty] | PF.phsB | cVal.mag.f
[8 empty] | PF.phsC | cVal.mag.f
[8 empty] | PF.neut | cVal.mag.f
[8 empty] | Z.phsA | cVal.mag.f
[8 empty] | Z.phsB | cVal.mag.f
[8 empty] | Z.phsC | cVal.mag.f
[8 empty] | Z.neut | cVal.mag.f
[8 empty] | Str | general
dirGeneral
phsA
dirPhsA
phsB
dirPhsB
phsC
dirPhsC
neut
dirNeut
[8 empty] | Op | general
phsA
phsB
phsC
neut
[8 empty] | OpEx | general
phsA
phsB
phsC
neut
[8 empty] | OpIn | general
phsA
phsB
phsC
neut
[8 empty] | OpCls | general
phsA
phsB
phsC
neut
[8 empty] | AutoRecSt | stVal
[8 empty] | Rel | stVal
[8 empty] | InsAlm | stVal
[8 empty] | PresAlm | stVal
[8 empty] | DenAlm | stVal
[8 empty] | TmpAlm | stVal
[8 empty] | GasInsAlm | stVal
[8 empty] | GasInsTr | stVal
[8 empty] | OpCnt | stVal
[8 empty] | BlkOpn | Oper.ctlVal
stVal
[8 empty] | BlkCls | Oper.ctlVal
stVal
[8 empty] | CBOpCap | stVal
[8 empty] | SwTyp | stVal
[8 empty] | SwOpCap | stVal
[8 empty] | EEHealth | stVal
[8 empty] | TapChg | Oper.ctlVal
valWTr.posVal
[8 empty] | EndPosR | stVal
[8 empty] | EndPosL | stVal
[8 empty] | ColPosA | mag.f
[8 empty] | ColTapPos | Oper.ctlVal
valWTr.posVal